**SIX MONTH SURVEILLANCE**

**HOMOGENEOUS ACBM RECORDS**

Date of Inspection:

District: Colusa Unified School District Inspector:

School: District Office Building: Old Jr./Sr. High School

|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Material  Class | Material | Homo. Mat. # | % Asb. | Ft2((S)/L.F.(L) | Location | Condition: Code & Comments | Friable  Yes/No |
| S | PLASTER | 01 | ASSUMED | UNDETERMINED | ALL WALLS AND CEILINGS THROUGHOUT BUILDING | (1) (4) | N |
| S | WALLBOARD WITH TEXTURE | 02 | ASSUMED | UNDETERMINED | ADMINISTRATIVE OFFICES ON FIRST FLOOR | (1) (4) | N |
| M | CARPET GLUE | 03 | ASSUMED | UNDETERMINED | ADMINISTRATIVE OFFICES, CLASSROOMS AND AUDITORIUM FOYER | (1) (4) | N |
| M | 12" VFT & MASTIC | 04 | ASSUMED | UNDETERMINED | MAIN CORRIDOR OF FIRST FLOOR | (1) (4) | N |
| M | LINOLEUM | 05 | ASSUMED | 100 S | SOUTH FOYER AND RESTROOMS (4) | (1) (4) | N |
| M | SHEET VINYL FLOORING | 06 | ASSUMED | UNDETERMINED | MAIN CORRIDOR OF SECOND FLOOR, STAIRWELLS AND AUDITORIUM | (1) (4) | N |
| M | A/C TRANSITE PANELS | 07 | ASSUMED | 35 S | WALLS AND HOOD OF BOOTH IN SCIENCE ROOM ON SECOND FLOOR | (12) COULD NOT LOCATE | N |
| T | AIRCELL PIPE INSULATION | 08 | ASSUMED | UNKNOWN | IN WALLS THROUGHOUT ATTIC, FIRST AND SECOND FLOORS | (11) | Y |

Z:\Clients\Colusa Unified School District\14-3310 3 Year Reinspections\Sites\District Office\District Office - 6 month.wpd

CONDITION CODE

General Condition: (1) Good (2) Damaged (3) Significantly Damaged (25% or more)

Change in Condition: (4) No (5) Yes (If Yes, explain under comments)

Abated: (6) Repaired (7) Removed (8) Encapsulated (9) Enclosed (10) Isolated & Restricted

Miscellaneous: (11) Inaccessible, no inspection data (12) Other (Explain under comments) (13) Non-Asbestos/Not Inspected

(14) Non AHERA/Not Inspected

**CONSULT ORIGINAL AND SUPPLEMENTARY INSPECTION REPORTS FOR MATERIALS WITH TRACE AMOUNTS OF ASBESTOS**