## District Summary
Proposition 39: California Clean Energy Jobs Act Energy Expenditure Plan
District Site Summary
Campus | Annual Electric Savings (kWh) | Annual Natural Gas Savings (therms) | Annual Cost Energy Savings ($) | A&E & Commissioning Soft Cost | Bid Activities PM / CM Soft Cost | Contingency / Escalation | Other Soft Cost DSA Inspector | Measure Cost ($) | Incentives / Rebates | Non Repayable Funds (Avoided Labor Cost) | Total Project Cost | EEM SIR
Burchfield Elementary School | 98352.7674 | 140 | 22161.4265 | 13269.728 | 14243.8597 | 13786.5477 | 1960.4592 | 215814.4414 | 0 |  | 215814.4414
Egling Middle School | 130511.2614 | 637 | 22252.072 | 9586.6 | 11053.9635 | 11612.4108 | 1339.635 | 180190.7443 | 0 |  | 180190.7443
Colusa High School | 121540.3418 | 911 | 20750.761 | 8502.208 | 9325.0705 | 10060.2164 | 1068.6312 | 166361.8311 | 1000 |  | 165361.8311
TOTALS: | 350404.3706 | 1688 | 65164.2595 | 31358.536 | 34622.8937 | 35459.1749 | 4368.7254 | 562367.0168 | 1000 | 0 | 561367.0168 | 1.68
Year 1 Prop 39 Funding / Planning $$ | 112836
Year 2 | 111253
Approx. Years 3,4 & 5 (3 x $112,836) | 338508 | [9 empty] | Proposed Measure Costs | 562367.0168
Approximate Available Funding | 562597 | [9 empty] | Minus Incentives / Rebates | 1000
[11 empty] | Prop 39 Share | 561367.0168
[11 empty] | Delta - Under Budget | 1229.9832

## Burchfield ES
Burchfield Elementary School
Energy Conservation Measures | [19 empty] | ***Savings Capped per CEC guidelines |  | ***Savings Capped per CEC guidelines
ECM # | ECM Description | Audit/Survey | Scope | Area | Product | Picture | Next Action | Who for Next Action | Quantity | Mat'l Cost | Labor | Direct Construction Sub-Total | A&E & Commissioning Soft Cost | Bid Activities PM / CM Soft Cost | Contingency / Escalation | Other Soft Cost | Total Measure Cost | Non Repayable Funding | Incentives / Rebates | Annual Electric Savings | Annual Gas Savings | Annual Energy Savings | SIR
[10 empty] | per fixture |  |  | 10% | 10% | 8% | DSA Inspector 1.5% | $$ | Avoided Labor Costs or Rebates |  | kWh | therms | $$ | P39 Calc | % of Cap Limit
1a | Implement "automatic shutdown" software on all computers. | Digital Energy - Bright Schools | Software and Programming | Library - Computers |  |  |  |  | 30 | 43 | 0 | 1290 | 0 | 0 | 103.2 | 0 | 1393.2 |  | 0 | 11913.55 | 0 | 2740.1165 | 7.85 | 1
2 | Wireless Thermostats/Door Sensors | Digital Energy - Bright Schools | Replacement of all programmable thermostats with web programable wireless thermostats including door sensors to cycle off HVAC equipment when door is left open. | Check audit for specific rooms. | Wireless Thermostat and sensors- Manufacturer TBD |  |  |  | 31 | 314.236 | Labor by District Staff | 9741.3167 | 0 | 974.1317 | 779.3053 |  | 11494.7538 |  | 0 | 8832 | 311 | 2286.38 | 3.05
3a | Lighting Exterior -Replacement of exterior Metal Halide (MH) fixtures with LED | Digital Energy - Bright Schools | MH 400W to LED 148W 130W | ECM-3 Calcs indicates locations. | Lithonia DSXF3 |  |  |  | 2 | 1000 | Labor of $125 included in Material Cost | 2000 | 200 | 200 | 160 | 0 | 2560 |  | 0 | 820 |  | 141 | 1.02
3b | Exterior Lighting Controls | Digital Energy - Bright Schools | Exterior Smart Controls | ECM-3 Calcs indicates locations. | Add-on to Lithonia Fixture |  |  |  | 2 | 111 | Labor will be part of Fixture Install | 222 | 0 | 0 | 0 | 0 | 222 |  | 0 | 790.2174 |  | 181.75 | 6.51
4a | Interior Lighting Lamp Replacement | Digital Energy - Bright Schools | Replace T8 32W lamps with LED lamps. | ECM-4a Tab indicates locations | Phillips 14.5W LED 48" T8 Lamp |  |  |  | 1354 | 17.75 | Labor Included in Materials Cost | 24033.5 | 0 | 0 | 1922.68 |  | 30891.51 | 0 | 0 | 34921 | -206 | 7336 | 3.59
4a-i | Interior Lighting Lamp Replacement | Digital Energy - Bright Schools | LED Re-lamping Ballast Replacement (25%) | ECM-4a Tab indicates locations | Phillips 120-277V 2-Lamp F32T8 Ballast |  |  |  | 169.25 | 27 | Labor Included in Materials Cost | 4569.75 | 0 | 0 | 365.58
5a | HVAC Pkg Gas/Elec Replacements | Digital Energy - Bright Schools | Replace all-electric wall-mount heat pumps with high efficiency units with economizers | Portables 19-23 | 4-Ton |  |  |  | 5 | 5992 | 3500 | 47460 | 4746 | 4746 | 3796.8 | 711.9 | 61460.7 |  | 0 | 21315 | 0 | 4902.45 | 1.37
5b | HVAC Pkg Gas/Elec Replacements | Digital Energy - Bright Schools | Replace gas-heating wall-mount heat pumps with high efficiency units with economizers | Portables 3-7 & 24-25 | 3.5-Ton |  |  |  | 7 | 8391.04 | 3500 | 83237.28 | 8323.728 | 8323.728 | 6658.9824 | 1248.5592 | 107792.2776 |  | 0 | 19761 | 35 | 4573.73 | 0.84
[11 empty] | TOTALS | 172553.8467 | 13269.728 | 14243.8597 | 13786.5477 | 1960.4592 | 215814.4414 | 0 | 0 | 98352.7674 | 140 | 22161.4265 | 1.56
Total Lighting Capped at 15% of Total kWH use by Site
|  |  |  | Proposed Measure Costs | 215814.4414 | [13 empty] | Total kWh Usage at Site | 238271
|  |  |  | Minus non-Repayable Funds | 0 | [13 empty] | 15% Cap | 35740.65
|  |  |  | Prop 39 Share | 215814.4414 | [13 empty] | Lighting KWh Savings | 35741
[19 empty] | Delta | -0.35
Total HVAC Savings Capped at 25% of Total kWH use by Site
[19 empty] | Total kWh Usage at Site | 238271
[19 empty] | 25% Cap | 59567.75
[19 empty] | HVAC KWh Savings | 41076
[19 empty] | Delta | 18491.75
Total Plug Load Savings Capped at 5% of Total kWH use by Site
[19 empty] | Total kWh Usage at Site | 238271
[19 empty] | 5% Cap | 11913.55
[19 empty] | Plug Load KWh Savings | 11913.55 |  |  |  | Lighting Cap Reduction Req'd
[19 empty] | Delta | 0 |  |  |  | -1654.45
Note on L16: Sharon Thomas: Using $3,250 per district direction instead of $4,500 which was quote from mfr. Representative.

## Egling MS
Egling Middle School
Energy Conservation Measures | [19 empty] | ***Savings Capped per CEC guidelines |  | ***Savings Capped per CEC guidelines
ECM # | ECM Description | Audit/Survey | Scope | Area | Product | Picture | Next Action | Who for Next Action | Quantity | Mat'l Cost | Labor | Direct Construction Sub-Total | A&E & Commissioning Soft Cost | Bid Activities PM / CM Soft Cost | Contingency / Escalation | Other Soft Cost | Total Measure Cost | Non Repayable Funding | Incentives / Rebates | Annual Electric Savings | Annual Gas Savings | Annual Energy Savings | SIR
[10 empty] | per fixture |  |  | 10% | 10% | 8% | DSA Inspector 1.5% | $$ | Avoided Labor Costs or Rebates |  | kWh | therms | $$ | P39 Calc | % of Cap Limit
1a | Implement "automatic shutdown" software on all computers. | Digital Energy - Bright Schools | Software and Programming | Library - Computers |  |  |  |  | 50 | 43 |  | 2150 | 0 | 0 | 172 | 0 | 2322 |  | 0 | 22019 | 0 | 3368.907 | 5.81 | 1
1b | PVC strip curtains for walk in refrigerator | Digital Energy - Bright Schools | Installation of PVC strip curtains at door to walk in refrigerator | Kitchen |  |  |  |  | 1 | 234 | 35 | 269 |  |  | 21.52 |  | 290.52 |  | 0 | 1406 |  | 215 | 3
2 | Wireless Thermostats/Door Sensors | Digital Energy - Bright Schools | Replacement of all programmable thermostats with web programmable wireless thermostats including door sensors to cycle off HVAC equipment when door is left open. | Check audit for specific rooms. | Wireless Thermostat and Sensor- Manufacturer TBD |  |  |  | 49 | 299.4619 | Labor by District Staff | 14673.635 | 0 | 1467.3635 | 1173.8908 |  | 17314.8893 |  | 0 | 17226 | 634 | 2968.428 | 2.66
3a | Lighting Exterior -Replacement of exterior High Pressure Sodium (HPS) fixtures with LED | Digital Energy - Bright Schools | HPS 50W to LED 25W | ECM-3 Calcs indicates locations. | Cree XSPW - 25W |  |  |  | 1 | 367 | Labor of $125 included in Material Cost | 367 | 36.7 | 36.7 | 29.36 | 0 | 469.76 |  | 0 | 128 |  | 19.584 | 0.85
3b | Lighting Exterior -Replacement of exterior Metal Halide (MH) fixtures with LED | Digital Energy - Bright Schools | MH 100W to LED 42W | ECM-3 Calcs indicates locations. | Cree XSPW - 42W |  |  |  | 10 | 419 | Labor of $125 included in Material Cost | 4190 | 419 | 419 | 335.2 | 0 | 5363.2 |  | 0 | 2774 |  | 424.422 | 1.36
3c | Lighting Exterior -Replacement of exterior Metal Halide (MH) fixtures with LED | Digital Energy - Bright Schools | MH 400W to LED 148W | ECM-3 Calcs indicates locations. | Lithonia DSXF3 |  |  |  | 2 | 1000 | Labor of $125 included in Material Cost | 2000 | 200 | 200 | 160 | 0 | 2560 |  | 0 | 2263 |  | 346.239 | 2.15
3d | Exterior Lighting Controls | Digital Energy - Bright Schools | Exterior Smart Controls | ECM-3 Calcs indicates locations. | Add-on to 11 Cree Fixtures & 2 Lithonia Fixtures. Both about the same price |  |  |  | 13 | 111 | Labor will be part of Fixture Install | 1443 | 0 | 0 | 0 | 0 | 1443 |  | 0 | 1320.2614 |  | 202 | 1.23
4a | Interior Lighting Lamp Replacement | Digital Energy - Bright Schools | Replace T8 32W lamps with LED lamps. | ECM-4a Tab indicates locations | Phillips 14.5W LED 48" T8 Lamp |  | ECM-4a Tab indicatees locations |  | 1508 | 17.75 | Labor is Included in Materials | 26767 |  |  | 2141.36 |  | 34405.02 |  | 0 | 49186 |  | 9475 | 4.12
4a-i | Interior Lighting Lamp Replacement | Digital Energy - Bright Schools | LED Re-lamping Ballast Replacement (25%) | As Needed | Phillips 120-277V 2-Lamp F32T8 Ballast |  |  |  | 188.5 | 27 | Labor is Included in Materials | 5089.5 |  |  | 407.16
4c | Interior Lighting Lamp Replacment | Digital Energy - Bright Schools | Replace F32T8-U lamp in the 2x2 Troffer Fixtures with F25T8 Lamps | Classrroms: 102,101,119,120,129,100,214,210,203,204 | Phillips 25W 6" gap T8 U-Lamp |  |  |  | 20 | 15 | 2 | 340 | 0 | 0 | 27.2 |  | 367.2 |  | 0 | 584 |  | 89.352 | 3.66
5a | HVAC Pkg Gas/Elec Replacements | Digital Energy - Bright Schools | Replace all-electric wall-mount heat pumps with high efficiency units with economizers | Portables 2-3 | 3.5 Ton Nominal |  |  |  | 2 | 5591 | 3500 | 18182 | 1818.2 | 1818.2 | 1454.56 | 272.73 | 72714.25 |  | 0 | 25232 | 0 | 3860.496 | 0.99
5a | HVAC Pkg Gas/Elec Replacements | Digital Energy - Bright Schools | Replace all-electric wall-mount heat pumps with high efficiency units with economizers | Portables 1, 2, 3, 4, 8, 9 | 3.8 & 4 Ton Nominal |  |  |  | 4 | 5992 | 3500 | 37968 | 3796.8 | 3796.8 | 3037.44 | 569.52
5b | HVAC Pkg Gas/Elec Replacements | Digital Energy - Bright Schools | Replace gas-heating wall-mount heat pumps with high efficiency units with economizers | Portables 5-7 | 4-Ton Nominal |  |  |  | 3 | 7553 | 3500 | 33159 | 3315.9 | 3315.9 | 2652.72 | 497.385 | 42940.905 |  | 0 | 8373 | 3 | 1282.644 | 0.67
[12 empty] | 146598.135 | 9586.6 | 11053.9635 | 11612.4108 | 1339.635 | 180190.7443 | 0 | 0 | 130511.2614 | 637 | 22252.072 | 1.77
|  |  |  | Proposed Measure Costs | 180190.7443 | [11 empty] | Total Lighting Capped at 15% of Total kWH use by Site
|  |  |  | Minus non-Repayable Funds | 0 | [13 empty] | Total kWh Usage at Site | 440390
|  |  |  | Prop 39 Share | 180190.7443 | [13 empty] | 15% Cap | 66058.5
[19 empty] | Lighting KWh Savings | 54935
[19 empty] | Delta | 11123.5
Total HVAC Savings Capped at 25% of Total kWH use by Site
[19 empty] | Total kWh Usage at Site | 440390
[19 empty] | 25% Cap | 110097.5
[19 empty] | HVAC KWh Savings | 33605
[19 empty] | Delta | 76492.5
Total Plug Load Savings Capped at 5% of Total kWH use by Site
[19 empty] | Total kWh Usage at Site | 440390
[19 empty] | 5% Cap | 22019.5
[19 empty] | Plug Load KWh Savings | 22019 |  |  |  | Plug Load Cap Reduction Req'd
[19 empty] | Delta | 0.5 |  |  |  | -594
Note on U6: Cassie Baugher: Reduced by 594 kWh to meet cap

## Colusa HS
Colusa High School
Energy Conservation Measures
ECM # | ECM Description | Audit/Survey | Scope | Area | Product | Picture | Next Action | Who for Next Action | Quantity | Mat'l Cost | Labor | Direct Construction Sub-Total | A&E & Commissioning Soft Cost | Bid Activities PM / CM Soft Cost | Contingency / Escalation | Other Soft Cost | Total Measure Cost | Non Repayable Funding | Incentives / Rebates | Annual Electric Savings | Annual Gas Savings | Annual Energy Savings | SIR
[13 empty] | 10% | 10% | 8% | DSA Inspector 1.5% | $$ | Avoided Labor Costs or Rebates |  | kWh | therms | $$ | P39 Calc
1a | Implement "automatic shutdown" software on all computers. | Digital Energy - Bright Schools | Software and Programming | Library - Computers |  |  |  |  | 50 | 43 | 0 | 2150 | 0 | 0 | 172 | 0 | 2322 |  | 0 | 22613 | 0 | 3573 | 6.16
1b | PVC strip curtains for walk in freezer and refrigerator | Digital Energy - Bright Schools | Installation of PVC strip curtains at door to walk in freezer and refrigerator | Kitchen |  |  |  |  | 2 | 234 | 35 | 538 | 0 | 0 | 43.04 | 0 | 581.04 |  | 0 | 4414 |  | 697 | 4.82 | Not included in Plug Load Cap Count
1c | Occupancy Sensor Controller for Vending Machine | Digital Energy - Bright Schools | Installation of occupancy sensor to shut down cold drink vending machine during non-occupancy periods. |  | Vending Miser |  |  |  | 1 | 285 |  | 285 | 0 | 0 | 0 | 0 | 285 |  | 0 | 1533 |  | 242 | 4.27
2 | Wireless Thermostats/Door Sensors | Digital Energy - Bright Schools | Replacement of all programmable thermostats with web programmable wireless thermostats including door sensors to cycle off HVAC equipment when door is left open. | Check audit for specific rooms. | Wireless Thermostat and Sensors- Manufacturer TBD |  |  |  | 25 | 329.145 | Labor by District Staff | 8228.625 | 0 | 822.8625 | 658.29 |  | 9709.7775 |  | 0 | 7944 | 901 | 1654.295 | 2.65
3a | Lighting Exterior -Replacement of exterior High Pressure Sodium (HPS) fixtures with LED | Digital Energy - Bright Schools | HPS 100W to LED 42W | ECM-3 Calcs indicates locations. | Cree XSPW - 42W |  |  |  | 20 | 419 | Labor of $125 included in Material Cost | 8380 | 838 | 838 | 670.4 | 0 | 10726.4 |  | 0 | 5329 |  | 841.982 | 1.35
3b | Lighting Exterior -Replacement of exterior Metal Halide (MH) fixtures with LED | Digital Energy - Bright Schools | HPS 150W to LED 42W | ECM-3 Calcs indicates locations. | Cree XSPW - 42W |  |  |  | 8 | 675 | Labor of $125 included in Material Cost | 5400 | 540 | 540 | 432 | 0 | 6912 |  | 0 | 5011 |  | 791.738 | 1.86
3c | Exterior Lighting Controls | Digital Energy - Bright Schools | Exterior Smart Controls | ECM-3 Calcs indicates locations. | Add-on to Cree Fixtures |  |  |  | 28 | 111 | Labor will be part of Fixture Install | 3108 | 0 | 0 | 0 | 0 | 3108 |  | 0 | 2487.3418 |  | 393 | 1.13
4a | Interior Lighting Lamp Replacement | Digital Energy - Bright Schools | Replace T8 32W lamps with LED lamps. | ECM-4a Tab indicatees locations | Phillips 14.5W LED 48" T8 Lamp |  |  |  | 1340 | 17.75 | Labor is Included in Material Cost | 23785 | 0 | 0 | 1902.8 | 0 | 30849.12 |  | 0 | 43707 | 0 | 8050 | 3.92
4a-i | Interior Lighting Lamp Replacement | Digital Energy - Bright Schools | LED Re-lamping Ballast Replacement (25%) | As Needed | Phillips 120-277V 2-Lamp F32T8 Ballast |  |  |  | 177 | 27 | Labor is Included in Material Cost | 4779 | 0 | 0 | 382.32 | 0
4d | Interior Lighting Fixture Replacment | Digital Energy - Bright Schools | Replace 38 2-F32T8 Fixtures with 20 43W LED Fixtures | Gymnasium Boys & Girls Locker rooms | Hubbell Sedona SCP 43W |  | Fixtures already installed. Need to send in rebate |  | 20 | 143 | Labor & Tax is Included in Material Cost | 2860 | 0 | 0 | 0 | 0 | 2860 |  | 1000 | 1540 |  | 243.32 | 2.28
5a | HVAC Pkg Gas/Elec Replacements | Digital Energy - Bright Schools | Replace all-electric wall-mount heat pumps with high efficiency units with economizers | 700 Wing - Unit 33, 34 & 35 MPR - Units 3 & 4 | 4-Ton |  |  |  | 5 | 5992 | 3500 | 47460 | 4746 | 4746 | 3796.8 | 711.9 | 61460.7 |  | 0 | 21315 | 0 | 3367.77 | 1.02
5b | HVAC Pkg Gas/Elec Replacements | Digital Energy - Bright Schools | Replace gas-heating wall-mount heat pumps with high efficiency units with economizers | Portables: 800 Wing | 3.5 Ton |  |  |  | 2 | 8391.04 | 3500 | 23782.08 | 2378.208 | 2378.208 | 1902.5664 | 356.7312 | 30797.7936 | 0 | 0 | 5646 | 10 | 896.498 | 0.66
6 | Skylights | N/A | Replace (19) 4x4 skylights throughout the Gymnasium | Boys & Girls Locker-rooms, Kitchen, Custodial, Service Area, Boys & Girls Coaches/Trainer Areas | SunOptics Signature Series Dome Skylights |  |  |  | 19 | 350 | Labor by District Staff for Install | 6650 | 0 | 0 | 100 | 0 | 6750 |  | 0 | 1 |  | 0.158 | 0.31
[12 empty] | 137405.705 | 8502.208 | 9325.0705 | 10060.2164 | 1068.6312 | 166361.8311 | 0 | 1000 | 121540.3418 | 911 | 20750.761 | 1.72
|  |  |  | Proposed Measure Costs | 166361.8311 | [11 empty] | Total Lighting Capped at 15% of Total kWH use by Site
|  |  |  | Minus non-Repayable Funds or Rebates | 1000 | [13 empty] | Total kWh Usage at Site | 533847
|  |  |  | Prop 39 Share | 165361.8311 | [13 empty] | 15% Cap | 80077.05
[19 empty] | Lighting KWh Savings | 55587
[19 empty] | Delta | 24490.05
Total HVAC Savings Capped at 50% of Total kWH use by Site
[19 empty] | Total kWh Usage at Site | 533847
[19 empty] | 25% Cap | 133461.75
[19 empty] | HVAC KWh Savings | 26961
[19 empty] | Delta | 106500.75
Total Plug Load Savings Capped at 5% of Total kWH use by Site
[19 empty] | Total kWh Usage at Site | 533847
[19 empty] | 5% Cap | 26692.35
[19 empty] | Plug Load KWh Savings | 24146
[19 empty] | Delta | 2546.35
Note on M10: Sharon Thomas: Installing contractor cost per kW audit. Includes material cost/labor sub O and P, mark up, taxes, programming, start up, testing etc.

## Cash Flow
Colusa Unified School District
Prop 39 California Clean Energy Jobs Act
Project Implementation - 5 Year Cash Flow Summary
|  | FY 13-14 | FY 14-15 | FY 15-16 | FY 16-17 | FY 17-18 | TOTALS
|  | Year 1 (Received) | Year 2 | Year 3 (Jan 2016) | Year 4 (Jan 2017) | Year 5 (Jan 2018) |  | [1]
Annual State Funding Allocation |  | 112836 | 111253 | 112836 | 112836 | 112836 | 562597
| Remaining Funds Available for Projects: | 112836 | 111253 | 112836 | 112836 | 112836 | 562597
Anticipated Project Expenditures
Energy Conservation Measures all Campuses |  |  |  | 561367 |  |  | 561367
0
0
| Total Estimated Project Expenditures: | 0 | 0 | 561367 | 0 | 0 | 561367
| Projected Funding Carried Over from Year to Year: | 112836 | 224089 | -224442 | -111606 | 1230 | 1230 | [2]
Notes:
[1] | Allocation for Year 3, 4 and 5 is Estimated
[2] | There is currently $1,230 in uncommitted Prop 39 funding

## Uti Rates
Lookup Rate Sheet
School | Elec Rate | Gas Rate | GSF | kWh | therms
Burchfield Primary | 0.22 | 0.82 | 34587 | 238271 | 4098
Egling MS | 0.2 | 0.525 | 50438 | 440390 | 8647
Colusa HS | 0.19 | 0.443 | 77559 | 533847 | 25200
Data taken from Bright Schools Audit Dated 5/13/15

## ECM-1a Proj E3
ECM 1a / Digital Energy Project E3 - Networked Software Desktop Power-down Program
Power-Down Program
School | Computers Qty | Est Software Cost/ Computer | Rebate/ Computer | Total Cost/School | Total Rebate/ School | Rate | Existing PC Consumption (kWh) | Existing PC Energy Consumption ($) | Annual Electrical Savings (kWh) | Annual Energy Savings ($) | Data Pulled directly from Digital Energy Summary
Burchfield Primary | 30 | 43 | 15 | 1290 | 450 |  | 35503 |  | 13568 | 3121
Egling MS | 50 | 43 | 15 | 2150 | 750 |  | 35503 |  | 22613 | 3460
Colusa HS | 50 | 43 | 15 | 2150 | 750 |  | 21302 |  | 22613 | 3573

## ECM-1b Proj E2
ECM 1b / Digital Energy Project E2 - PVC Strip Curtains
PVC Strip Curtains for Walk-in Freezers and Refrigeratros
School Site | Building or Space# | Unit Qty | Notes | Est Unit Cost/ Machine | Labor/ Unit | Rebate/ Install | Total Cost/School | Total Rebate/ School | kW Saved | kWh Saved | Rate | Energy Cost Savings | Data Pulled directly from Digital Energy Summary
Egling MS |  | 1 |  | 234 | 35 | 0 | 234 | 0 |  | 1406 | 0.153 | 215
Colusa HS |  | 2 |  | 234 | 35 | 0 | 538 | 0 |  | 4414 | 0.158 | 697

## ECM-1c Proj E1
ECM 1c / Digital Energy Project E-1 - Vending Machine Occupancy Sensors
VendingMiser
School Site | Building or Space# | Vending Qty | Occupoancy Sensor? | Lights On? | Notes | Est Unit Cost/ Machine | Rebate/ Machine | Total Cost/School | Total Rebate/ School | kW Saved | kWh Saved | Rate | Energy Cost Savings | Data Pulled directly from Digital Energy Summary
Burchfield Primary |  | 0 |  |  |  | 43 | 15 | 0 | 0
[8 empty] | 0 | 0
[8 empty] | % Rebate to Cost | #DIV/0!
Egling MS |  | 0 |  |  |  | 43 | 15 | 0 | 0
[8 empty] | 0 | 0
[8 empty] | % Rebate to Cost | #DIV/0!
Colusa HS |  | 1 |  |  |  | 285 | 100 | 285 | 100 | 0 | 1533 | 0.158 | 242
[8 empty] | 285 | 0 | 0 | 1533 | 0.158 | 242
[8 empty] | 100 | 0%

## ECM-2 Proj M5
ECM 2 / Digital Energy Project M5 - Pelican Wireless HVAC Controls and EMS
|  | Per Pelican Unit |  |  | Site
Burchfield Primary | Qty | Material Cost | Labor Cost | Total UnitCost | Material Cost | Labor Cost | Taxes (7.5%) | Direct Total Cost |  | Electrical Rate ($) | Gas Rate ($) | Existing Energy Consumption (kWh) | Existing Energy Consumption (Therms) | Existing Energy Consumption ($/kWh) | Existing Energy Consumption ($/Therms) | Proposed Energy Consumption (kWh) | Proposed Energy Consumption (Therms) | Proposed Energy Consumption ($/kWh) | Proposed Energy Consumption ($/Therms) | Annual Eelctrical Savings (kWh) | Annual Gas Savings (Therms) | Annual Energy Savings ($)
Demo existing thermostats | 31 |  |  | 0 | 0 | 0 | 0 | 0 | 0
Pelican Wireless Thermostats | 31 | 175 |  | 175 | 5425 | 0 | 406.875 | 5831.875
Pelican Gateway (1/Site typically) | 1 | 147 |  | 147 | 147 | 0 | 11.025 | 158.025
Pelican Extended Repeater (1/Bldg Typically) | 5 | 109 |  | 109 | 545 | 0 | 40.875 | 585.875
Pelican Wireless Door Sensor | 31 | 92 |  | 92 | 2852 | 0 | 213.9 | 3065.9
Pelican Subscription Price/Stat/Year | 31 | 2.99 |  | 2.99 | 92.69 | 0 | 6.9518 | 99.6418
Wall Architectural Modifications | 31 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
Programming, Start-up and Testing | 31 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 292.3126 | 9061.69 | 0 | 679.6267 | 9741.3167 | 0 | 0.23 | 0.82 | 88322 | 3108 | 20314.06 | 2548.56 | 79490 | 2797 | 18282.7 | 2293.54 | 8832 | 311 | 2286.38
Labor will be performed by District Staff | [6 empty] | Cost per Room | 314.236
Formula Driven
Data Pulled from Digital Energy Audit
Pulled from RateTable Tab
Rebates (No longer avaiable for this type project)
Total Project Budget | [8 empty] | 9741.3167
Cost/Unit | [8 empty] | 314.236
|  | Per Unit |  |  | Site
Egling MS | Qty | Material Cost | Labor Cost | Total UnitCost | Material Cost | Labor Cost | Taxes (7.5%) | Direct Total Cost |  | Electrical Rate ($) | Gas Rate ($) | Existing Energy Consumption (kWh) | Existing Energy Consumption (Therms) | Existing Energy Consumption ($/kWh) | Existing Energy Consumption ($/Therms) | Proposed Energy Consumption (kWh) | Proposed Energy Consumption (Therms) | Proposed Energy Consumption ($/kWh) | Proposed Energy Consumption ($/Therms) | Annual Eelctrical Savings ($) | Annual Gas Savings ($) | Annual Energy Savings ($)
Demo existing thermostats | 49 |  |  | 0 | 0 | 0 | 0 | 0
Pelican Wireless Thermostats | 49 | 175 |  | 175 | 8575 | 0 | 643.125 | 9218.125
Pelican Gateway (1/Site typically) | 1 | 147 |  | 147 | 147 | 0 | 0 | 147
Pelican Extended Repeater (1/Bldg Typically) | 6 | 109 |  | 109 | 654 | 0 | 0 | 654
Pelican Wireless Door Sensor | 49 | 92 |  | 92 | 4508 | 0 | 0 | 4508
Pelican Subscription Price/Stat/Year | 49 | 2.99 |  | 2.99 | 146.51 | 0 | 0 | 146.51
Wall Architectural Modifications | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Programming, Start-up and Testing | 49 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 286.3369 | 14030.51 | 0 | 643.125 | 14673.635 | 0 | 0.153 | 0.525 | 172260 | 6339 | 26355.78 | 3327.975 | 155034 | 5705 | 23720.202 | 2995.125 | 17226 | 634 | 2968.428
[7 empty] | Cost per Room | 299.4619
Formula Driven
Data Pulled from Digital Energy Audit
Pulled from RateTable Tab
0
Rebates (No longer avaiable for this type project)
Total Project Budget | [8 empty] | 14673.635
Cost/Unit | [8 empty] | 299.4619
|  | Per Unit |  |  | Site
CHS | Qty | Material Cost | Labor Cost | Total UnitCost | Material Cost | Labor Cost | Taxes (7.5%) | Direct Total Cost |  | Electrical Rate ($) | Gas Rate ($) | Existing Energy Consumption (kWh) | Existing Energy Consumption (Therms) | Existing Energy Consumption ($/kWh) | Existing Energy Consumption ($/Therms) | Proposed Energy Consumption (kWh) | Proposed Energy Consumption (Therms) | Proposed Energy Consumption ($/kWh) | Proposed Energy Consumption ($/Therms) | Annual Eelctrical Savings ($) | Annual Gas Savings ($) | Annual Energy Savings ($)
Demo existing thermostats | 25 |  |  | 0 | 0 | 0 | 0 | 0
Pelican Wireless Thermostats | 25 | 175 |  | 175 | 4375 | 0 | 328.125 | 4703.125
Pelican Gateway (1/Site typically) | 1 | 147 |  | 147 | 147 | 0 | 11.025 | 158.025
Pelican Extended Repeater (1/Bldg Typically) | 7 | 109 |  | 109 | 763 | 0 | 57.225 | 820.225
Pelican Wireless Door Sensor | 25 | 92 |  | 92 | 2300 | 0 | 172.5 | 2472.5
Pelican Subscription Price/Stat/Year | 25 | 2.99 |  | 2.99 | 74.75 | 0 | 0 | 74.75
Wall Architectural Modifications | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Programming, Start-up and Testing | 25 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 306.39 | 7659.75 | 0 | 568.875 | 8228.625 | 0 | 0.158 | 0.443 | 79442 | 9007 | 12551.836 | 3990.101 | 71498 | 8106 | 11296.684 | 3590.958 | 7944 | 901 | 1654.295
[7 empty] | Cost per Room | 329.145
General Contractor O&P | [12 empty] | Formula Driven
Construction Contingency | 10% | [11 empty] | Data Pulled from Digital Energy Audit
Pulled from RateTable Tab
Construction with Contingency | [8 empty] | 0
Softcost (10% of Total Direct) | 10%
Rebates (No longer avaiable for this type project) | [8 empty] | 0
Total Project Budget | [8 empty] | 8228.625
Cost/Unit | [8 empty] | 329.145
Material Cost for Pelican Equipment came from RSD
Labor Cost from DigitaL Energy
No PG&E Rebates available - they were formerly.

## ECM-3 Proj L-6a
ECM 3a-3c Exterior Fixture Replacement / Digital Energy Project# L-6A
| General |  |  |  | Current | [14 empty] | Post Installation | [13 empty] | Savings
| Site | Bldg/Space | Space | Area Description | Current Fixt Code | Fixt Qty | Fixt Type | Bulb Type | #Bulbs per Fixture | Watts per Bulb | Opeating Hours | Total Watts/Line Item W/out Ballast | Ops Hrs/ Year | Manual Switch? | Photo Cell? | Time Clock? | Time Clock Schedule | EMS? | Pre KWh/yr | New Fixt Code | Post Fixt Qty | Fixture Type | Bulb Type | Watts/ Bulb WITH Ballast | Watts/Per Line Item | Cost with Labor per Fixture | Rebate/ Fixture | Cost for all Fixtures per Line Item | Ops Hrs/Year | Photo Cell? | EMS? | Operating Hours | kWh/Yr | Retro Lighting kWh Saved/Line Item | Annual Energy Savings | Notes
ECM 3a | Burchfield Primary |  |  |  |  | 2 | Pole Light | MH | 1 | 458 |  | 916 | [8 empty] | 2 | Lithonia DSXF3 | LED | 148 | 296 | 1000 | [7 empty] | 2528.24 | 581.68 | Switched from 130W noted in Audit to 148W, and adjusted savings using Digital Energy Calculator
ECM 3a | Egling MS - Band Room |  |  |  |  | 1 | WP ? | HPS | 1 | 50 | 3650 | 50 | [8 empty] | 1 | Cree XSPW - 25W | LED | 25 | 25 | 367 | [5 empty] | 1825 |  | 128 | 19.584 | Switched from 420W noted in Audit to 25W, and adjusted savings using Digital Energy Calculator
ECM 3b | Egling MS |  |  |  |  | 10 | WP-? | MH | 1 | 100 | 3650 | 1000 | [8 empty] | 10 | Cree XSPW - 42W | LED | 42 | 420 | 419 | [5 empty] | 1825 |  | 2774 | 424.422
ECM 3c | Egling MS |  |  |  |  | 2 | FL-? | MH | 1 | 400 | 3650 | 800 | [8 empty] | 2 | Lithonia DSXF3 | LED | 148 | 296 | 1000 | [5 empty] | 1825 |  | 2263 | 346.239 | Switched from 130W noted in Audit to 148W, so 12% less savings than shown on audit
ECM 3a | Colusa HS |  |  |  |  | 20 | WP? | HPS | 1 | 100 | 3650 | 2000 | [8 empty] | 20 | Cree XSPW - 42W | LED | 42 | 840 | 419 | [5 empty] | 1825 |  | 5329 | 841.982 | Switched from 46W noted in audit to 42W, and adjusted savings using Digital Energy Calculator
ECM 3b | Colusa HS |  |  |  |  | 8 | FL? | MH | 1 | 150 | 4380 | 1200 | [8 empty] | 8 | Cree XSPW - 42W | LED | 42 | 336 | 675 | [5 empty] | 2190 |  | 5011 | 791.738 | Switched from 46W noted in audit to 42W, and adjusted savings using Digital Energy Calculator
ECM - Exterior SMART Controls Digital / Energy Project# L-6B
| Site |  |  |  |  | Control QYT | Control Cost/Unit | Control Cost Energy Savings | Electricity Rate | Annual Electrical Savings
ECM 3b | Burchfield Primary |  |  |  |  | 6 | 111 | 181.75 | 0.23 | 790.2174
ECM 3d | Egling MS |  |  |  |  | 13 | 111 | 202 | 0.153 | 1320.2614
ECM 3c | Colusa HS |  |  |  |  | 28 | 111 | 393 | 0.158 | 2487.3418
Multi-level sensor ordered with Cree fixture for additional $111.
Multi-level sensor ordered with Lithonia fixture for addiotnal $100.

## ECM-3 Calcs
Site | ID | Source ID | Building | Room # | Plan ID | Room Type | Existing Fixture Type | Fixture Style | Fixture Height (ft.) | Existing Fixture Count (Single) | Existing Fixture Count (Tandem) | Old Fixture Burn Out Qty | Existing Lamp Type | Existing Ballast Type | Proposed Retrofit Type | Make and Model | Total Retrofit Qty | New Lamps Required | New Ballast Configuration | New Lamp Type | New Ballast Type | Proposed Control Type | Control Qty | Relay Qty | Retrofit Complexity | Control Complexity | Ceiling Type | Notes | Foot Candles Before | Foot Candles After | Existing Watts Per Fixture | Proposed Watts Per Fixture | Hours of Operation Now | Retrofit Savings (kWh) | Hours of Operation After | Control Savings (kWh)
Burchfield | 58 | 58 | Parking Lot | Parking Lot |  | Exterior | MH-400W | Surface |  | 2 |  |  |  |  | LED-130W |  | 2 | (2)-130W-LED |  |  |  | Exterior Smart Controls | 2 | [5 empty] | 45 |  | 458 | 130 | 4380 | 2873.28 | 2190 | 569.4
Site | ID | Source ID | Building | Room # | Plan ID | Room Type | Existing Fixture Type | Fixture Style | Fixture Height (ft.) | Existing Fixture Count (Single) | Existing Fixture Count (Tandem) | Old Fixture Burn Out Qty | Existing Lamp Type | Existing Ballast Type | Proposed Retrofit Type | Make and Model | Total Retrofit Qty | New Lamps Required | New Ballasts Required | New Lamp Type | New Ballast Type | Proposed Control Type | Control Qty | Relay Qty | Retrofit Complexity | Control Complexity | Ceiling Type | Notes | Foot Candles Before | Foot Candles After | Existing Watts Per Fixture | Proposed Watts Per Fixture | Hours of Operation Now | Retrofit Savings (kWh) | Hours of Operation After | Control Savings (kWh)
Egling | 78 | 78 | Exterior | Exterior |  | Exterior-Existing Photocell | MH-100W | Surface |  | 10 |  |  |  |  | LED-42W |  | 10 | (10)-42W-LED |  |  |  | Exterior Smart Controls | 10 | [7 empty] | 118 | 42 | 3650 | 2774 | 1825 | 766.5
Egling | 91 | 91 | Exterior | Exterior |  | Exterior-Existing Photocell | MH-400W | Surface |  | 2 |  |  |  |  | LED-148W |  | 2 | (2)-148W-LED |  |  |  | Exterior Smart Controls | 2 | [7 empty] | 458 | 148 | 3650 | 2263 | 1825 | 540.2
Egling | 93 | 93 | Band Room | Band Room |  | Exterior-Existing Photocell | HPS-50W | Surface |  | 1 |  |  |  |  | LED-25W |  | 1 | (1)-25W-LED |  |  |  | Exterior Smart Controls | 1 | [7 empty] | 60 | 25 | 3650 | 127.75 | 1825 | 45.625
Site | ID | Source ID | Building | Room # | Plan ID | Room Type | Existing Fixture Type | Fixture Style | Fixture Height (ft.) | Existing Fixture Count (Single) | Existing Fixture Count (Tandem) | Old Fixture Burn Out Qty | Existing Lamp Type | Existing Ballast Type | Proposed Retrofit Type | Make and Model | Total Retrofit Qty | New Lamps Required | New Ballasts Configuration | New Lamp Type | New Ballast Type | Proposed Control Type | Control Qty | Relay Qty | Retrofit Complexity | Control Complexity | Ceiling Type | Notes | Foot Candles Before | Foot Candles After | Existing Watts Per Fixture | Proposed Watts Per Fixture | Hours of Operation Now | Retrofit Savings (kWh) | Hours of Operation After | Control Savings (kWh)
CHS | 19 | 19 | Exterior | Exterior |  | Exterior-Existing Photocell | HPS-100W | Surface |  | 20 |  |  |  |  | LED-42W |  | 20 | (20)-42W-LED |  |  |  | Exterior Smart Controls | 20 | [7 empty] | 115 | 42 | 3650 | 5329 | 1825 | 1533
CHS | 35 | 35 | Exterior | Exterior |  | Exterior | MH-150W |  |  | 8 |  |  |  |  | LED-42W |  | 8 | (8)-42W-LED |  |  |  | Exterior Smart Controls | 8 | [7 empty] | 185 | 42 | 4380 | 5010.72 | 2190 | 735.84

## ECM-4 Proj L1
ECM - 4a & 4b / Digital Energy Project L1 & L2 - Colusa Interior Lighting Counts and Wattages
Legend F-Tube = Florescent Tube U-Tube = Bipin U-Bent Tube C-Tube = Circline Tube CSM = Ceiling Surface Mount WSM = Wall Surface Mount | [5 empty] | Burchfield Primary | Egling MS | Colusa HS
Current Item | Watts | # Lamps | Size | Mount | Type Bulb |  |  |  |  | Notes
T-8 32W | 32 | 2 |  |  |  | 1354 | 1508 | 1416
T-8 32W-U | 32 | 1 |  |  |  | 0 | 20 | 0
ECM-4a-Calculated using Digital Energy Calculator in WorkSummaries
New Item | [5 empty] | LED-Tube 14W | LED-Tube 14W | LED-Tube 14W
Watts | [5 empty] | 14 | 14 | 14
# Units | [5 empty] | 1354 | 1508 | 1416 |  | More fixtures for Egling & Burchfield had some already T828W so not proposed for T8 Relamping above
kW Saved
kWh Saved | [5 empty] | 61139 | 81093 | 56606 |  | Includes Operating Hour Detail
Rate ($kWh) | [5 empty] | 0.23 | 0.153 | 0.158
Cost/Unit | [5 empty] | 17.75 | 17.75 | 17.75
District Labor | [5 empty] | Inc in Mat | Inc in Mat | Inc in Mat
Annual Energy Savings ($) | [5 empty] | 14061.97 | 12407.229 | 8943.748
Rebate/Unit | [5 empty] | 0 | 0 | 0
Total Rebate | [5 empty] | 0 | 0 | 0 |  | Rebate is POS & included in cost of lamp
SIR
ECM-4a-i
New Item | [5 empty] | Ballast (25%) | Ballast (25%) | Ballast (25%)
Watts
# Units | [5 empty] | 169.25 | 188.5 | 177
kW Saved
kWh Saved
Rate ($kWh)
Cost/Unit | [5 empty] | 27 | 27 | 27
District Labor | [5 empty] | Inc in Mat | Inc in Mat | Inc in Mat
Annual Electric Savings (kWh) | [5 empty] | 0 | 0 | 0 |  | No Savings to this, just cost
Annual Energy Savings ($) | [5 empty] | 0 | 0 | 0 |  | No Savings to this, just cost
Rebate/Unit | [5 empty] | 0 | 0 | 0 |  | No Savings to this, just cost
Total Rebate | [5 empty] | 0 | 0 | 0 | N/A | No Savings to this, just cost
SIR | [5 empty] | Included with LED Re-lamping Cost |  |  |  | No Savings to this, just cost
[7 empty] | Colusa HS |  |  | See cut sheets below
ECM-4D 2 Lamp 32W Fixture to 43W LED Fixture (1/2 as many fixtures needed) | [6 empty] | Current | Proposed
New Item | [6 empty] | 2-F28T8 | Hubbel-SCP
Watts | [6 empty] | 55 | 43
# Units | [6 empty] | 38 | 20
Hours of Operation | [6 empty] | 3500 | 3500
Rate ($kWh) | [6 empty] | 0.158 | 0.158
Cost/Unit | [7 empty] | 143
District Labor | [7 empty] | 0 |  | Labor included with Fixture
Annual Electric Savings (kWh) | [7 empty] | 1540 |  | Chuck working on this
Annual Energy Savings ($) | [7 empty] | 243.32 |  | Chuck working on this
Rebate/Unit | [7 empty] | 50
Total Rebate | [7 empty] | 1000
SIR
ECM- 4C F32TE-U to F25T8-U
New Item | [6 empty] | F25T8-U
Watts | [6 empty] | 25
# Units | [6 empty] | 20
kW Saved
kWh Saved
Rate ($kWh) | [6 empty] | 0.153
Cost/Unit | [6 empty] | 15
District Labor | [6 empty] | 2
Annual Electric Savings (kWh) | [6 empty] | 584
Annual Energy Savings ($) | [6 empty] | 89.352
Rebate/Unit | [6 empty] | 0
Total Rebate | [6 empty] | 0
SIR

## ECM-4a Inventory
Site | ID | Source ID | Building | Room # | Plan ID | Room Type | Existing Fixture Type | Fixture Style | Fixture Height (ft.) | Existing Fixture Count (Single) | # Lamps | Existing Fixture Count (Tandem) | Old Fixture Burn Out Qty | Existing Lamp Type | Existing Ballast Type | Proposed Retrofit Type | Make and Model | Total Retrofit Qty | New Lamps Required | New Ballast Configuration | New Lamp Type | New Ballast Type | Proposed Control Type | Control Qty | Relay Qty | Retrofit Complexity | Control Complexity | Ceiling Type | Notes | Foot Candles Before | Foot Candles After | Existing Watts Per Fixture | Proposed Watts Per Fixture | Hours of Operation Now | Retrofit Savings (kWh) | Hours of Operation After | Control Savings (kWh)
Burchfield | 82 | 82 | Portables | 22 |  | Classroom | 2-F28T8 | 2x4 Troffer |  | 12 | 24 |  |  | Standard | Electronic IS | 14W LED Tubes | [6 empty] | OS-3 | 1 | 1 |  |  |  |  | 56 |  | 48 | 28 | 1950 | 0 | 1560 | 102.96
Burchfield | 84 | 84 | Portables | 25 |  | Classroom | 2-F28T8 | 2x4 Troffer |  | 12 | 24 |  |  | Standard | Electronic IS | 14W LED Tubes | [6 empty] | OS-3 | 1 | 1 |  |  |  |  | 56 |  | 48 | 28 | 1950 | 0 | 1560 | 102.96
Burchfield | 19 | 19 | Ford Building | Men's Restroom |  | Restroom | 2-F32T8 | 1x4 Wrap |  | 2 | 4 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 2 | (4)-F28T8 | (2)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 27 |  | 64 | 28 | 2340 | 196.56 | 1872 | 20.592
Burchfield | 20 | 20 | Ford Building | Women's Restroom |  | Restroom | 2-F32T8 | 1x4 Wrap |  | 2 | 4 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 2 | (4)-F28T8 | (2)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 27 |  | 64 | 28 | 2340 | 196.56 | 1872 | 20.592
Burchfield | 21 | 21 | Ford Building | Spanish Library |  | Offices | 2-F32T8 | 2x4 Wrap |  | 4 | 8 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 4 | (8)-F28T8 | (4)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 30 |  | 64 | 28 | 2340 | 393.12 | 1872 | 41.184
Burchfield | 23 | 23 | Kinder Building | Lounge & Storage |  | Offices | 2-F32T8 | 2x4 Troffer |  | 12 | 24 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 12 | (24)-F28T8 | (12)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 5 |  |  |  |  | 70 |  | 64 | 28 | 2340 | 1179.36 | 1872 | 123.552
Burchfield | 25 | 25 | Kinder Building | Main Office |  | Offices | 2-F32T8 | 2x4 Wrap |  | 6 | 12 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 6 | (12)-F28T8 | (6)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 2 |  |  |  |  | 83 |  | 64 | 28 | 2340 | 589.68 | 1872 | 61.776
Burchfield | 26 | 26 | Kinder Building | Hallways |  | Hallways | 2-F32T8 | 1x4 Troffer |  | 3 | 6 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 3 | (6)-F28T8 | (3)-2-F28T8 | Standard | Electronic IS | [7 empty] | 50 |  | 64 | 28 | 1950 | 245.7 | 1950 | 0
Burchfield | 27 | 27 | Kinder Building | Hallways |  | Hallways | 2-F32T8 | 1x4 Troffer |  | 4 | 8 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 4 | (8)-F28T8 | (4)-2-F28T8 | Standard | Electronic IS | [7 empty] | 50 |  | 64 | 28 | 1950 | 327.6 | 1950 | 0
Burchfield | 28 | 28 | Kinder Building | 1 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 20 | 40 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 20 | (40)-F28T8 | (20)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 78 |  | 64 | 28 | 1950 | 1638 | 1560 | 171.6
Burchfield | 29 | 29 | Kinder Building | 1 |  | Workroom | 2-F32T8 | 2x4 Troffer |  | 3 | 6 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 3 | (6)-F28T8 | (3)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 78 |  | 64 | 28 | 1950 | 245.7 | 1560 | 25.74
Burchfield | 30 | 30 | Kinder Building | Men's Restroom |  | Restroom | 2-F32T8 | 1x4 Wrap |  | 3 | 6 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 3 | (6)-F28T8 | (3)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 50 |  | 64 | 28 | 2340 | 294.84 | 1872 | 30.888
Burchfield | 31 | 31 | Kinder Building | Women's Restroom |  | Restroom | 2-F32T8 | 1x4 Wrap |  | 3 | 6 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 3 | (6)-F28T8 | (3)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 50 |  | 64 | 28 | 2340 | 294.84 | 1872 | 30.888
Burchfield | 32 | 32 | Kinder Building | 2 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 21 | 42 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 21 | (42)-F28T8 | (21)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 50 |  | 64 | 28 | 1950 | 1719.9 | 1560 | 180.18
Burchfield | 33 | 33 | Kinder Building | 2 |  | Workroom | 2-F32T8 | 2x4 Troffer |  | 3 | 6 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 3 | (6)-F28T8 | (3)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 50 |  | 64 | 28 | 1950 | 245.7 | 1560 | 25.74
Burchfield | 34 | 34 | Kinder Building | 3 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 22 | 44 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 22 | (44)-F28T8 | (22)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 78 |  | 64 | 28 | 1950 | 1801.8 | 1560 | 188.76
Burchfield | 35 | 35 | Kinder Building | 3 |  | Workroom | 2-F32T8 | 2x4 Troffer |  | 3 | 6 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 3 | (6)-F28T8 | (3)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 78 |  | 64 | 28 | 1950 | 245.7 | 1560 | 25.74
Burchfield | 37 | 37 | Kinder Building | Outside Storage |  | Exterior | 2-F32T8 | 2x4 Surface |  | 2 | 4 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 2 | (4)-F28T8 | (2)-2-F28T8 | Standard | Electronic IS | [7 empty] | 25 |  | 64 | 28 | 4380 | 367.92 | 4380 | 0
Burchfield | 43 | 43 | Admin Building | Kitchen |  | Kitchen | 2-F32T8 | 2x4 Wrap |  | 1 | 2 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 1 | (2)-F28T8 | (1)-2-F28T8 | Standard | Electronic IS | [9 empty] | 64 | 28 | 1560 | 65.52 | 1560 | 0
Burchfield | 45 | 45 | Admin Building | Server Room |  | Server Room | 2-F32T8 | 2x4 Troffer |  | 1 | 2 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 1 | (2)-F28T8 | (1)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 108 |  | 64 | 28 | 180 | 7.56 | 144 | 0.792
Burchfield | 46 | 46 | Admin Building | Teachers Room |  | Teachers Room | 2-F32T8 | 2x4 Troffer |  | 9 | 18 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 9 | (18)-F28T8 | (9)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 2 |  |  |  |  | 77 |  | 64 | 28 | 2160 | 816.48 | 1728 | 85.536
Burchfield | 47 | 47 | Admin Building | Main Entry |  | Offices | 2-F32T8 | 2x4 Troffer |  | 4 | 8 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 4 | (8)-F28T8 | (4)-2-F28T8 | Standard | Electronic IS | [9 empty] | 64 | 28 | 2340 | 393.12 | 2340 | 0
Burchfield | 48 | 48 | Admin Building | Main Office |  | Offices | 2-F32T8 | 2x4 Troffer |  | 12 | 24 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 12 | (24)-F28T8 | (12)-2-F28T8 | Standard | Electronic IS | [7 empty] | 25 |  | 64 | 28 | 2340 | 1179.36 | 2340 | 0
Burchfield | 49 | 49 | Admin Building | Nurse |  | Offices | 2-F32T8 | 2x4 Troffer |  | 2 | 4 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 2 | (4)-F28T8 | (2)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 | [6 empty] | 64 | 28 | 2340 | 196.56 | 1872 | 20.592
Burchfield | 50 | 50 | Admin Building | Private Office 1 |  | Offices | 2-F32T8 | 2x4 Troffer |  | 4 | 8 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 4 | (8)-F28T8 | (4)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 | [6 empty] | 64 | 28 | 2340 | 393.12 | 1872 | 41.184
Burchfield | 51 | 51 | Admin Building | Private Office 2 |  | Offices | 2-F32T8 | 2x4 Troffer |  | 2 | 4 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 2 | (4)-F28T8 | (2)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 | [6 empty] | 64 | 28 | 2340 | 196.56 | 1872 | 20.592
Burchfield | 52 | 52 | Admin Building | Private Office 3 |  | Offices | 2-F32T8 | 2x4 Troffer |  | 3 | 6 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 3 | (6)-F28T8 | (3)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 | [6 empty] | 64 | 28 | 2340 | 294.84 | 1872 | 30.888
Burchfield | 53 | 53 | Admin Building | Workroom/Storage |  | Offices | 2-F32T8 | 2x4 Troffer |  | 4 | 8 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 4 | (8)-F28T8 | (4)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 | [6 empty] | 64 | 28 | 2340 | 393.12 | 1872 | 41.184
Burchfield | 54 | 54 | Admin Building | Men's Restroom |  | Restroom | 2-F32T8 | 1x4 Wrap |  | 2 | 4 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 2 | (4)-F28T8 | (2)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 | [6 empty] | 64 | 28 | 2340 | 196.56 | 1872 | 20.592
Burchfield | 55 | 55 | Admin Building | Women's Restroom |  | Restroom | 2-F32T8 | 1x4 Wrap |  | 2 | 4 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 2 | (4)-F28T8 | (2)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 | [6 empty] | 64 | 28 | 2340 | 196.56 | 1872 | 20.592
Burchfield | 56 | 56 | Admin Building | Library |  | Library | 2-F32T8 | 2x4 Troffer |  | 29 | 58 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 29 | (58)-F28T8 | (29)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 | [6 empty] | 64 | 28 | 1950 | 2375.1 | 1560 | 248.82
Burchfield | 59 | 59 | Annex | Hallways |  | Hallways | 2-F32T8 | 1x4 Surface |  | 16 | 32 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 16 | (32)-F28T8 | (16)-2-F28T8 | Standard | Electronic IS | [7 empty] | 45 |  | 64 | 28 | 1950 | 1310.4 | 1950 | 0
Burchfield | 60 | 60 | Annex | 18 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 27 | 54 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 27 | (54)-F28T8 | (27)-2-F28T8 | Standard | Electronic IS | [7 empty] | 45 |  | 64 | 28 | 1950 | 2211.3 | 1950 | 0
Burchfield | 61 | 61 | Annex | 17 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 26 | 52 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 26 | (52)-F28T8 | (26)-2-F28T8 | Standard | Electronic IS | [7 empty] | 45 |  | 64 | 28 | 1950 | 2129.4 | 1950 | 0
Burchfield | 62 | 62 | Annex | 16 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 13 | 26 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 13 | (26)-F28T8 | (13)-2-F28T8 | Standard | Electronic IS | [7 empty] | 45 |  | 64 | 28 | 1950 | 1064.7 | 1950 | 0
Burchfield | 63 | 63 | Annex | 15 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 13 | 26 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 13 | (26)-F28T8 | (13)-2-F28T8 | Standard | Electronic IS | [7 empty] | 45 |  | 64 | 28 | 1950 | 1064.7 | 1950 | 0
Burchfield | 64 | 64 | Annex | 14 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 26 | 52 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 26 | (52)-F28T8 | (26)-2-F28T8 | Standard | Electronic IS | [7 empty] | 45 |  | 64 | 28 | 1950 | 2129.4 | 1950 | 0
Burchfield | 65 | 65 | Annex | 13 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 26 | 52 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 26 | (52)-F28T8 | (26)-2-F28T8 | Standard | Electronic IS | [7 empty] | 45 |  | 64 | 28 | 1950 | 2129.4 | 1950 | 0
Burchfield | 66 | 66 | Annex | 12 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 26 | 52 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 26 | (52)-F28T8 | (26)-2-F28T8 | Standard | Electronic IS | [7 empty] | 45 |  | 64 | 28 | 1950 | 2129.4 | 1950 | 0
Burchfield | 67 | 67 | Annex | Men's Restroom |  | Restroom | 2-F32T8 | 1x4 Wrap |  | 1 | 2 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 1 | (2)-F28T8 | (1)-2-F28T8 | Standard | Electronic IS | Photocell Controller | 1 | 1 |  |  |  |  | 45 |  | 64 | 28 | 2340 | 98.28 | 1404 | 20.592
Burchfield | 68 | 68 | Annex | Women's Restroom |  | Restroom | 2-F32T8 | 1x4 Wrap |  | 1 | 2 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 1 | (2)-F28T8 | (1)-2-F28T8 | Standard | Electronic IS | Photocell Controller | 1 | 1 |  |  |  |  | 45 |  | 64 | 28 | 2340 | 98.28 | 1404 | 20.592
Burchfield | 80 | 80 | Portables | 21 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 12 | 24 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 12 | (24)-F28T8 | (12)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 30 |  | 64 | 28 | 1950 | 982.8 | 1560 | 102.96
Burchfield | 3 | 3 | Portables | 4 |  | Classroom | 4-F32T8 | 2x4 Troffer |  | 10 | 40 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 10 | (40)-F28T8 | (10)-4-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 128 | 28 | 1950 | 2067 | 1560 | 85.8
Burchfield | 5 | 5 | Portables | 5 |  | Classroom | 4-F32T8 | 2x4 Troffer |  | 10 | 40 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 10 | (40)-F28T8 | (10)-4-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 128 | 28 | 1950 | 2067 | 1560 | 85.8
Burchfield | 7 | 7 | Portables | 6 |  | Classroom | 4-F32T8 | 2x4 Troffer |  | 10 | 40 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 10 | (40)-F28T8 | (10)-4-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 128 | 28 | 1950 | 2067 | 1560 | 85.8
Burchfield | 9 | 9 | Portables | 7 |  | Classroom | 4-F32T8 | 2x4 Troffer |  | 10 | 40 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 10 | (40)-F28T8 | (10)-4-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 128 | 28 | 1950 | 2067 | 1560 | 85.8
Burchfield | 11 | 11 | Ford Building | 8 |  | Classroom | 4-F32T8 | 2x4 Troffer |  | 9 | 36 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 9 | (36)-F28T8 | (9)-4-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 46 |  | 128 | 28 | 1950 | 1860.3 | 1560 | 77.22
Burchfield | 13 | 13 | Ford Building | 9 |  | Classroom | 4-F32T8 | 2x4 Troffer |  | 9 | 36 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 9 | (36)-F28T8 | (9)-4-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 46 |  | 128 | 28 | 1950 | 1860.3 | 1560 | 77.22
Burchfield | 15 | 15 | Ford Building | 10 |  | Classroom | 4-F32T8 | 2x4 Troffer |  | 9 | 36 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 9 | (36)-F28T8 | (9)-4-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 46 |  | 128 | 28 | 1950 | 1860.3 | 1560 | 77.22
Burchfield | 17 | 17 | Ford Building | 11 |  | Classroom | 4-F32T8 | 2x4 Troffer |  | 9 | 36 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 9 | (36)-F28T8 | (9)-4-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 46 |  | 128 | 28 | 1950 | 1860.3 | 1560 | 77.22
Burchfield | 40 | 40 | Admin Building | Cafateria |  | Cafateria | 4-F32T8 | 4x4 Box |  | 16 | 64 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 16 | (64)-F28T8 | (16)-4-F28T8 | Standard | Electronic IS | OS-3 | 4 | 4 |  |  |  |  | 35 |  | 128 | 28 | 2340 | 3968.64 | 1872 | 164.736
Burchfield | 42 | 42 | Admin Building | Kitchen |  | Kitchen | 4-F32T8 | 2x4 Troffer |  | 7 | 28 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 7 | (28)-F28T8 | (7)-4-F28T8 | Standard | Electronic IS | [7 empty] | 60 |  | 128 | 28 | 1560 | 1157.52 | 1560 | 0
Burchfield | 72 | 72 | Portables | 19 |  | Classroom | 4-F32T8 | 2x4 Troffer |  | 10 | 40 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 10 | (40)-F28T8 | (10)-4-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 30 |  | 128 | 28 | 1950 | 2067 | 1560 | 85.8
Burchfield | 74 | 74 | Portables | 20 |  | Classroom | 4-F32T8 | 2x4 Troffer |  | 10 | 40 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 10 | (40)-F28T8 | (10)-4-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 30 |  | 128 | 28 | 1950 | 2067 | 1560 | 85.8
Burchfield | 76 | 76 | Portables | 23 |  | Classroom | 4-F32T8 | 2x4 Troffer |  | 10 | 40 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 10 | (40)-F28T8 | (10)-4-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 30 |  | 128 | 28 | 1950 | 2067 | 1560 | 85.8
Burchfield | 78 | 78 | Portables | 24 |  | Classroom | 4-F32T8 | 2x4 Troffer |  | 10 | 40 |  |  | Standard | Electronic IS | 14W LED Tubes |  | 10 | (40)-F28T8 | (10)-4-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 30 |  | 128 | 28 | 1950 | 2067 | 1560 | 85.8
1354
Site | ID | Source ID | Building | Room # | Plan ID | Room Type | Existing Fixture Type | Fixture Style | Fixture Height (ft.) | Existing Fixture Count (Single) | # Lamps | Existing Fixture Count (Tandem) | Old Fixture Burn Out Qty | Existing Lamp Type | Existing Ballast Type | Proposed Retrofit Type | Make and Model | Total Retrofit Qty | New Lamps Required | New Ballasts Required | New Lamp Type | New Ballast Type | Proposed Control Type | Control Qty | Relay Qty | Retrofit Complexity | Control Complexity | Ceiling Type | Notes | Foot Candles Before | Foot Candles After | Existing Watts Per Fixture | Proposed Watts Per Fixture | Hours of Operation Now | Retrofit Savings (kWh) | Hours of Operation After | Control Savings (kWh)
Egling | 41 | 41 | Cafateria | Cafateria |  | Cafateria | 2-F28T8 | 2x4 Troffer |  | 30 | 60 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 30 |  | (2)-1-F32T8-U |  |  | OS-3 | 4 | 3 |  |  |  |  | 57 |  | 64 | 28 | 2160 | 2332.8 | 1728 | 362.88
Egling | 42 | 42 | Cafateria | Boys Restroom |  | Restrooms | 2-F28T8 | 1x4 Wrap |  | 3 | 6 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 3 |  | (2)-1-F32T8-U |  |  | OS-1 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 2160 | 233.28 | 1728 | 36.288
Egling | 43 | 43 | Cafateria | Girls Restroom |  | Restrooms | 2-F28T8 | 1x4 Wrap |  | 3 | 6 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 3 |  | (2)-1-F32T8-U |  |  | OS-1 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 2160 | 233.28 | 1728 | 36.288
Egling | 44 | 44 | Cafateria | Cafeteria Storage |  | Closet | 2-F28T8 | 2x4 Wrap |  | 2 | 4 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 2 |  | (2)-1-F32T8-U |  |  | OS-1 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 360 | 25.92 | 288 | 4.032
Egling | 46 | 46 | Cafateria | Kitchen |  | Kitchen | 2-F28T8 | 1x4 Troffer |  | 2 | 4 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 2 |  | (22)-2-F28T8 | [9 empty] | 35 |  | 64 | 28 | 1800 | 129.6 | 1800 | 0
Egling | 1 | 1 | Admin Office | Genral Office 1 |  | Office | 2-F32T8 | 2x4 Troffer |  | 8 | 16 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 8 | (16)-F28T8 | (8)-2-F28T8 | Standard | Electronic IS | [7 empty] | 44 |  | 64 | 28 | 2160 | 622.08 | 2160 | 0
Egling | 2 | 2 | Admin Office | Genral Office 2 |  | Office | 2-F32T8 | 2x4 Troffer |  | 6 | 12 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 6 | (12)-F28T8 | (6)-2-F28T8 | Standard | Electronic IS | [7 empty] | 44 |  | 64 | 28 | 2160 | 466.56 | 2160 | 0
Egling | 3 | 3 | Admin Office | Work Room |  | Office | 2-F32T8 | 2x4 Troffer |  | 3 | 6 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 3 | (6)-F28T8 | (3)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 44 |  | 64 | 28 | 2160 | 233.28 | 1728 | 36.288
Egling | 4 | 4 | Admin Office | Private Office 1 |  | Office | 2-F32T8 | 2x4 Troffer |  | 2 | 4 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 2 | (4)-F28T8 | (2)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 44 |  | 64 | 28 | 2160 | 155.52 | 1728 | 24.192
Egling | 5 | 5 | Admin Office | Private Office 2 |  | Office | 2-F32T8 | 2x4 Troffer |  | 2 | 4 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 2 | (4)-F28T8 | (2)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 44 |  | 64 | 28 | 2160 | 155.52 | 1728 | 24.192
Egling | 6 | 6 | Admin Office | Private Office 3 |  | Office | 2-F32T8 | 2x4 Troffer |  | 1 | 2 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 1 | (2)-F28T8 | (1)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 44 |  | 64 | 28 | 2160 | 77.76 | 1728 | 12.096
Egling | 7 | 7 | Admin Office | Nurse |  | Office | 2-F32T8 | 2x4 Troffer |  | 1 | 2 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 1 | (2)-F28T8 | (1)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 | [6 empty] | 64 | 28 | 2160 | 77.76 | 1728 | 12.096
Egling | 9 | 9 | Admin Office | Men's Restroom |  | Restrooms | 2-F32T8 | 1x4 Wrap |  | 1 | 2 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 1 | (2)-F28T8 | (1)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 | [6 empty] | 64 | 28 | 2160 | 77.76 | 1728 | 12.096
Egling | 10 | 10 | Admin Office | Women's Restroom |  | Restrooms | 2-F32T8 | 1x4 Wrap |  | 1 | 2 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 1 | (2)-F28T8 | (1)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 | [6 empty] | 64 | 28 | 2160 | 77.76 | 1728 | 12.096
Egling | 11 | 11 | 100 | Bldg. Common Area |  | Common Area | 2-F32T8 | 2x4 Troffer |  | 40 | 80 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 40 | (80)-F28T8 | (40)-2-F28T8 | Standard | Electronic IS | [7 empty] | 35 |  | 64 | 28 | 2160 | 3110.4 | 2160 | 0
Egling | 12 | 12 | 100 | Shared Work Room |  | Work Room | 2-F32T8 | 2x4 Troffer |  | 2 | 4 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 2 | (4)-F28T8 | (2)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 1800 | 129.6 | 1440 | 20.16
Egling | 13 | 13 | 100 | 104 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 17 | 34 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 17 | (34)-F28T8 | (17)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 3650 | 2233.8 | 2920 | 347.48
Egling | 14 | 14 | 100 | 102 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 19 | 38 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 19 | (38)-F28T8 | (19)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 2 |  |  |  |  | 35 |  | 64 | 28 | 3650 | 2496.6 | 2920 | 388.36
Egling | 16 | 16 | 100 | 101 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 16 | 32 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 16 | (32)-F28T8 | (16)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 3650 | 2102.4 | 2920 | 327.04
Egling | 18 | 18 | 100 | 103 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 17 | 34 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 17 | (34)-F28T8 | (17)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 3650 | 2233.8 | 2920 | 347.48
Egling | 19 | 19 | 100 | Closet |  | Closet | 2-F32T8 | 2x4 Wrap |  | 2 | 4 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 2 | (4)-F28T8 | (2)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 360 | 25.92 | 288 | 4.032
Egling | 20 | 20 | 100 | Men's Restroom |  | Restrooms | 2-F32T8 | 1x4 Wrap |  | 3 | 6 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 3 | (6)-F28T8 | (3)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 2160 | 233.28 | 1728 | 36.288
Egling | 21 | 21 | 100 | Women's Restroom |  | Restrooms | 2-F32T8 | 1x4 Wrap |  | 3 | 6 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 3 | (6)-F28T8 | (3)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 2160 | 233.28 | 1728 | 36.288
Egling | 22 | 22 | 100 | Men's Restroom |  | Restrooms | 2-F32T8 | 1x4 Wrap |  | 3 | 6 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 3 | (6)-F28T8 | (3)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 2160 | 233.28 | 1728 | 36.288
Egling | 23 | 23 | 100 | Women's Restroom |  | Restrooms | 2-F32T8 | 1x4 Wrap |  | 3 | 6 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 3 | (6)-F28T8 | (3)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 2160 | 233.28 | 1728 | 36.288
Egling | 27 | 27 | 100 | Shared Work Room |  | Work Room | 2-F32T8 | 2x4 Troffer |  | 2 | 4 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 2 | (4)-F28T8 | (2)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 1800 | 129.6 | 1440 | 20.16
Egling | 28 | 28 | 100 | 118 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 17 | 34 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 17 | (34)-F28T8 | (17)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 3650 | 2233.8 | 2920 | 347.48
Egling | 29 | 29 | 100 | 119 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 16 | 32 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 16 | (32)-F28T8 | (16)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 50 |  | 64 | 28 | 3650 | 2102.4 | 2920 | 327.04
Egling | 31 | 31 | 100 | 120 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 16 | 32 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 16 | (32)-F28T8 | (16)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 50 |  | 64 | 28 | 3650 | 2102.4 | 2920 | 327.04
Egling | 33 | 33 | 100 | 121 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 17 | 34 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 17 | (34)-F28T8 | (17)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 50 |  | 64 | 28 | 3650 | 2233.8 | 2920 | 347.48
Egling | 34 | 34 | 100 | Shared Work Room |  | Work Room | 2-F32T8 | 2x4 Troffer |  | 2 | 4 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 2 | (4)-F28T8 | (2)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 1800 | 129.6 | 1440 | 20.16
Egling | 35 | 35 | 100 | 129 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 16 | 32 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 16 | (32)-F28T8 | (16)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 50 |  | 64 | 28 | 3650 | 2102.4 | 2920 | 327.04
Egling | 37 | 37 | 100 | 130 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 10 | 20 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 10 | (20)-F28T8 | (10)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 2 |  |  |  |  | 50 |  | 64 | 28 | 3650 | 1314 | 2920 | 204.4
Egling | 38 | 38 | 100 | 131 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 16 | 32 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 16 | (32)-F28T8 | (16)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 50 |  | 64 | 28 | 3650 | 2102.4 | 2920 | 327.04
Egling | 39 | 39 | 100 | 100 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 4 | 8 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 4 | (8)-F28T8 | (4)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 2 |  |  |  |  | 50 |  | 64 | 28 | 3650 | 525.6 | 2920 | 81.76
Egling | 45 | 45 | Cafateria | Kitchen |  | Kitchen | 2-F32T8 | 1x4 Troffer |  | 22 | 44 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 22 | (44)-F28T8 | (22)-2-F28T8 | Standard | Electronic IS | [7 empty] | 35 |  | 64 | 28 | 1800 | 1425.6 | 1800 | 0
Egling | 47 | 47 | Gymnasium | Gymnasium |  | Gymnasium | 2-F32T8 | 1x4 Wrap |  | 48 | 96 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 48 | (96)-F28T8 | (48)-2-F28T8 | Standard | Electronic IS | Gym Lighting Controller | 1 | [5 empty] | 27 |  | 64 | 28 | 2400 | 4147.2 | 1680 | 967.68
Egling | 48 | 48 | Gymnasium | Storage |  | Storage | 2-F32T8 | 2x4 Wrap |  | 2 | 4 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 2 | (4)-F28T8 | (2)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 20 |  | 64 | 28 | 360 | 25.92 | 288 | 4.032
Egling | 50 | 50 | Gymnasium | Boys Locker Room |  | Locker Rooms | 2-F32T8 | 1x4 Wrap |  | 6 | 12 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 6 | (12)-F28T8 | (6)-2-F28T8 | Standard | Electronic IS | [7 empty] | 40 |  | 64 | 28 | 2520 | 544.32 | 2520 | 0
Egling | 51 | 51 | Gymnasium | Boys Locker Room |  | Locker Rooms | 2-F32T8 | 1x4 Wrap |  | 12 | 24 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 12 | (24)-F28T8 | (12)-2-F28T8 | Standard | Electronic IS | Photocell Controller | 1 | 1 |  |  |  |  | 40 |  | 64 | 28 | 2520 | 1088.64 | 1512 | 338.688
Egling | 52 | 52 | Gymnasium | Coach |  | Locker Rooms | 2-F32T8 | 1x4 Wrap |  | 6 | 12 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 6 | (12)-F28T8 | (6)-2-F28T8 | Standard | Electronic IS | [9 empty] | 64 | 28 | 2520 | 544.32 | 2520 | 0
Egling | 54 | 54 | Gymnasium | Boys Restroom |  | Locker Rooms | 2-F32T8 | 1x4 Wrap |  | 3 | 6 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 3 | (6)-F28T8 | (3)-2-F28T8 | Standard | Electronic IS | [9 empty] | 64 | 28 | 2520 | 272.16 | 2520 | 0
Egling | 56 | 56 | Gymnasium | Girls Locker Room |  | Locker Rooms | 2-F32T8 | 1x4 Wrap |  | 6 | 12 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 6 | (12)-F28T8 | (6)-2-F28T8 | Standard | Electronic IS | [7 empty] | 40 |  | 64 | 28 | 2520 | 544.32 | 2520 | 0
Egling | 57 | 57 | Gymnasium | Girls Locker Room |  | Locker Rooms | 2-F32T8 | 1x4 Wrap |  | 12 | 24 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 12 | (24)-F28T8 | (12)-2-F28T8 | Standard | Electronic IS | Photocell Controller | 1 | 1 |  |  |  |  | 40 |  | 64 | 28 | 2520 | 1088.64 | 1512 | 338.688
Egling | 58 | 58 | Gymnasium | Coach |  | Locker Rooms | 2-F32T8 | 1x4 Wrap |  | 6 | 12 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 6 | (12)-F28T8 | (6)-2-F28T8 | Standard | Electronic IS | [9 empty] | 64 | 28 | 2520 | 544.32 | 2520 | 0
Egling | 60 | 60 | Gymnasium | Girls Restroom |  | Locker Rooms | 2-F32T8 | 1x4 Wrap |  | 3 | 6 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 3 | (6)-F28T8 | (3)-2-F28T8 | Standard | Electronic IS | [9 empty] | 64 | 28 | 2520 | 272.16 | 2520 | 0
Egling | 63 | 63 | 200 | Bldg. Common Area |  | Common Area | 2-F32T8 | 2x4 Troffer |  | 34 | 68 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 34 | (68)-F28T8 | (34)-2-F28T8 | Standard | Electronic IS | [7 empty] | 24 |  | 64 | 28 | 2160 | 2643.84 | 2160 | 0
Egling | 64 | 64 | 200 | Men's Restroom |  | Restrooms | 2-F32T8 | 1x4 Wrap |  | 5 | 10 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 5 | (10)-F28T8 | (5)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 25 |  | 64 | 28 | 2160 | 388.8 | 1728 | 60.48
Egling | 65 | 65 | 200 | Women's Restroom |  | Restrooms | 2-F32T8 | 1x4 Wrap |  | 5 | 10 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 5 | (10)-F28T8 | (5)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 25 |  | 64 | 28 | 2160 | 388.8 | 1728 | 60.48
Egling | 66 | 66 | 200 | 214 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 18 | 36 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 18 | (36)-F28T8 | (18)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 3650 | 2365.2 | 2920 | 367.92
Egling | 68 | 68 | 200 | Shared Work Room |  | Work Room | 2-F32T8 | 2x4 Troffer |  | 4 | 8 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 4 | (8)-F28T8 | (4)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 1800 | 259.2 | 1440 | 40.32
Egling | 69 | 69 | 200 | 210 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 21 | 42 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 21 | (42)-F28T8 | (21)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 3650 | 2759.4 | 2920 | 429.24
Egling | 71 | 71 | 200 | Closet |  | Closet | 2-F32T8 | 2x4 Wrap |  | 2 | 4 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 2 | (4)-F28T8 | (2)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 25 |  | 64 | 28 | 360 | 25.92 | 288 | 4.032
Egling | 72 | 72 | 200 | 205 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 17 | 34 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 17 | (34)-F28T8 | (17)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 3650 | 2233.8 | 2920 | 347.48
Egling | 73 | 73 | 200 | 202 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 20 | 40 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 20 | (40)-F28T8 | (20)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 3650 | 2628 | 2920 | 408.8
Egling | 74 | 74 | 200 | 203 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 16 | 32 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 16 | (32)-F28T8 | (16)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 0 |  |  |  |  | 35 |  | 64 | 28 | 3650 | 2102.4 | 2920 | 327.04
Egling | 76 | 76 | 200 | 204 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 16 | 32 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 16 | (32)-F28T8 | (16)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 3650 | 2102.4 | 2920 | 327.04
Egling | 79 | 79 | Portables | 7 |  | Office | 2-F32T8 | 2x4 Troffer |  | 12 | 24 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 12 | (24)-F28T8 | (12)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 57 |  | 64 | 28 | 2160 | 933.12 | 1728 | 145.152
Egling | 81 | 81 | Portables | 8 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 12 | 24 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 12 | (24)-F28T8 | (12)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 57 |  | 64 | 28 | 3650 | 1576.8 | 2920 | 245.28
Egling | 83 | 83 | Portables | 9 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 12 | 24 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 12 | (24)-F28T8 | (12)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 57 |  | 64 | 28 | 3650 | 1576.8 | 2920 | 245.28
Egling | 85 | 85 | Portables | 5 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 10 | 20 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 10 | (20)-F28T8 | (10)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 60 |  | 64 | 28 | 3650 | 1314 | 2920 | 204.4
Egling | 87 | 87 | Portables | 6 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 10 | 20 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 10 | (20)-F28T8 | (10)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 60 |  | 64 | 28 | 3650 | 1314 | 2920 | 204.4
Egling | 89 | 89 | Portables | 4 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 12 | 24 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 12 | (24)-F28T8 | (12)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 57 |  | 64 | 28 | 3650 | 1576.8 | 2920 | 245.28
Egling | 92 | 92 | Choir Room | Choir Room |  | Choir Room | 2-F32T8 | 1x4 Wrap |  | 24 | 48 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 24 | (48)-F28T8 | (24)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 25 |  | 64 | 28 | 2160 | 1866.24 | 1728 | 290.304
Egling | 94 | 94 | Band Room | Band Room |  | Band Room | 2-F32T8 | 1x4 Wrap |  | 24 | 48 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 24 | (48)-F28T8 | (24)-2-F28T8 | Standard | Electronic IS | [7 empty] | 45 |  | 64 | 28 | 2160 | 1866.24 | 2160 | 0
Egling | 98 | 98 | Portables | 2 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 12 | 24 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 12 | (24)-F28T8 | (12)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 3650 | 1576.8 | 2920 | 245.28
Egling | 100 | 100 | Portables | 3 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 12 | 24 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 12 | (24)-F28T8 | (12)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 3650 | 1576.8 | 2920 | 245.28
Egling | 96 | 96 | Portables | 1 |  | Classroom | 4-F32T8 | 2x4 Troffer |  | 12 | 48 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 12 | (48)-F28T8 | (12)-4-F28T8 | Standard | Electronic IS | OS-3 | 1 | 2 |  |  |  |  | 35 |  | 128 | 28 | 3650 | 4380 | 2920 | 245.28
[11 empty] | 1508 | [6 empty] | 742 | [15 empty] | 179380
Site | ID | Source ID | Building | Room # | Plan ID | Room Type | Existing Fixture Type | Fixture Style | Fixture Height (ft.) | Existing Fixture Count (Single) | # Lamps | Existing Fixture Count (Tandem) | Old Fixture Burn Out Qty | Existing Lamp Type | Existing Ballast Type | Proposed Retrofit Type | Make and Model | Total Retrofit Qty | New Lamps Required | New Ballasts Configuration | New Lamp Type | New Ballast Type | Proposed Control Type | Control Qty | Relay Qty | Retrofit Complexity | Control Complexity | Ceiling Type | Notes | Foot Candles Before | Foot Candles After | Existing Watts Per Fixture | Proposed Watts Per Fixture | Hours of Operation Now | Retrofit Savings (kWh) | Hours of Operation After | Control Savings (kWh)
CHS | 1 | 1 | 100 | 100 |  | Offices | 2-F32T8 | 1x4 Box |  | 20 | 40 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 20 | (40)-F28T8 | (20)-2-F28T8 | Standard | Electronic IS | [7 empty] | 74 |  | 64 | 48 | 2400 | 768 | 2400 | 0
CHS | 2 | 2 | 100 | 102 |  | Offices | 2-F32T8 | 1x4 Box |  | 4 | 8 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 4 | (8)-F28T8 | (4)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 74 |  | 64 | 48 | 2400 | 153.6 | 1920 | 92.16
CHS | 3 | 3 | 100 | 104 |  | Offices | 2-F32T8 | 1x4 Box |  | 4 | 8 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 4 | (8)-F28T8 | (4)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 74 |  | 64 | 48 | 2400 | 153.6 | 1920 | 92.16
CHS | 4 | 4 | 100 | 101 |  | Offices | 2-F32T8 | 1x4 Box |  | 8 | 16 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 8 | (16)-F28T8 | (8)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 2 |  |  |  |  | 70 |  | 64 | 48 | 2400 | 307.2 | 1920 | 184.32
CHS | 5 | 5 | 100 | 105 |  | Offices | 2-F32T8 | 1x4 Box |  | 4 | 8 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 4 | (8)-F28T8 | (4)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 1 |  |  |  |  | 70 |  | 64 | 28 | 2400 | 345.6 | 1920 | 53.76
CHS | 6 | 6 | 100 | 109 |  | Library | 2-F32T8 | 8' Pendant Wrap |  | 30 | 60 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 30 | (60)-F28T8 | (30)-2-F28T8 | Standard | Electronic IS | OS-3 | 2 | 2 |  |  |  |  | 55 |  | 64 | 28 | 1800 | 1944 | 1440 | 302.4
CHS | 7 | 7 | 100 | 106 |  | Offices | 2-F32T8 | 1x4 Box |  | 10 | 20 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 10 | (20)-F28T8 | (10)-2-F28T8 | Standard | Electronic IS | [7 empty] | 70 |  | 64 | 28 | 2400 | 864 | 2400 | 0
CHS | 9 | 9 | 100 | 112 |  | Offices | 2-F32T8 | 1x4 Box |  | 10 | 20 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 10 | (20)-F28T8 | (10)-2-F28T8 | Standard | Electronic IS | [7 empty] | 40 |  | 64 | 28 | 2400 | 864 | 2400 | 0
CHS | 10 | 10 | 100 | 111 |  | Classroom | 2-F32T8 | 8' Pendant Wrap |  | 10 | 20 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 10 | (20)-F28T8 | (10)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 40 |  | 64 | 28 | 2160 | 777.6 | 1728 | 120.96
CHS | 11 | 11 | 100 | 113 |  | Classroom | 2-F32T8 | 1x4 Box |  | 4 | 8 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 4 | (8)-F28T8 | (4)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 40 |  | 64 | 28 | 2160 | 311.04 | 1728 | 48.384
CHS | 12 | 12 | 100 | 113 |  | Classroom | 2-F32T8 | 8' Pendant Wrap |  | 10 | 20 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 10 | (20)-F28T8 | (10)-2-F28T8 | Standard | Electronic IS | OS-3 | [6 empty] | 40 |  | 64 | 28 | 2160 | 777.6 | 1728 | 120.96
CHS | 16 | 16 | 100 | 114 |  | Lounge | 2-F32T8 | 1x4 Box |  | 10 | 20 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 10 | (20)-F28T8 | (10)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 2 |  |  |  |  | 40 |  | 64 | 28 | 1800 | 648 | 1440 | 100.8
CHS | 17 | 17 | 100 | 115 |  | Lounge | 2-F32T8 | 1x4 Box |  | 14 | 28 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 14 | (28)-F28T8 | (14)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 2 |  |  |  |  | 40 |  | 64 | 28 | 1800 | 907.2 | 1440 | 141.12
CHS | 18 | 18 | Exterior | Exterior |  | Exterior | 2-F32T8 | 1x4 Surface |  | 18 | 36 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 18 | (36)-F28T8 | (18)-2-F28T8 | Standard | Electronic IS | [9 empty] | 64 | 28 | 4380 | 2838.24 | 4380 | 0
CHS | 21 | 21 | 200 | 201 |  | Cafateria | 2-F32T8 | 1x4 Box |  | 24 | 48 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 24 | (48)-F28T8 | (24)-2-F28T8 | Standard | Electronic IS | [7 empty] | 40 |  | 64 | 28 | 2520 | 2177.28 | 2520 | 0
CHS | 23 | 23 | 200 | 202 |  | Kitchen | 2-F32T8 | 1x4 Wrap |  | 16 | 32 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 16 | (32)-F28T8 | (16)-2-F28T8 | Standard | Electronic IS | [7 empty] | 65 |  | 64 | 28 | 1800 | 1036.8 | 1800 | 0
CHS | 24 | 24 | 200 | 202 |  | Storage | 2-F32T8 | 1x4 Wrap |  | 8 | 16 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 8 | (16)-F28T8 | (8)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 2 |  |  |  |  | 55 |  | 64 | 28 | 360 | 103.68 | 288 | 16.128
CHS | 25 | 25 | 200 | 202 |  | Offices | 2-F32T8 | 1x4 Wrap |  | 2 | 4 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 2 | (4)-F28T8 | (2)-2-F28T8 | Standard | Electronic IS | [7 empty] | 45 |  | 64 | 28 | 2400 | 172.8 | 2400 | 0
CHS | 33 | 33 | 200 | 206 |  | Band Room | 2-F32T8 | 2x4 Box |  | 24 | 48 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 24 | (48)-F28T8 | (24)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 2 |  |  |  |  | 20 |  | 64 | 28 | 2520 | 2177.28 | 2016 | 338.688
CHS | 37 | 37 | 200 | Men's Locker Room |  | Coach's Room | 2-F32T8 | 1x4 Wrap |  | 2 | 4 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 2 | (4)-F28T8 | (2)-2-F28T8 | Standard | Electronic IS | [7 empty] | 25 |  | 64 | 28 | 2000 | 144 | 2000 | 0
CHS | 40 | 40 | 200 | Offices |  | Offices | 2-F32T8 | 1x4 Wrap |  | 5 | 10 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 5 | (10)-F28T8 | (5)-2-F28T8 | Standard | Electronic IS | [7 empty] | 20 |  | 64 | 28 | 2400 | 432 | 2400 | 0
CHS | 44 | 44 | 200 | Women's Locker Room |  | Coach's Room | 2-F32T8 | 1x4 Wrap |  | 4 | 8 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 4 | (8)-F28T8 | (4)-2-F28T8 | Standard | Electronic IS | [7 empty] | 20 |  | 64 | 28 | 2000 | 288 | 2000 | 0
CHS | 48 | 48 | 300 | 300 |  | Classroom | 2-F32T8 | 1x4 Wrap |  | 36 | 72 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 36 | (72)-F28T8 | (36)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 2160 | 2799.36 | 1728 | 435.456
CHS | 49 | 49 | 300 | 305 |  | Classroom | 2-F32T8 | 1x4 Wrap |  | 36 | 72 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 36 | (72)-F28T8 | (36)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 2160 | 2799.36 | 1728 | 435.456
CHS | 50 | 50 | 300 | 304 |  | Classroom | 2-F32T8 | 1x4 Wrap |  | 30 | 60 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 30 | (60)-F28T8 | (30)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 3 |  |  |  |  | 35 |  | 64 | 28 | 2160 | 2332.8 | 1728 | 362.88
CHS | 52 | 52 | 300 | 302 |  | Classroom | 2-F32T8 | 1x4 Wrap |  | 34 | 68 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 34 | (68)-F28T8 | (34)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 4 |  |  |  |  | 35 |  | 64 | 28 | 2160 | 2643.84 | 1728 | 411.264
CHS | 53 | 53 | 300 | 300 |  | Hallway | 2-F32T8 | 1x4 Wrap |  | 12 | 24 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 12 | (24)-F28T8 | (12)-2-F28T8 | Standard | Electronic IS | Photocell Controller | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 2520 | 1088.64 | 1512 | 338.688
CHS | 55 | 55 | 500 | 500 |  | Restrooms | 2-F32T8 | 1x4 Wrap |  | 4 | 8 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 4 | (8)-F28T8 | (4)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 2 |  |  |  |  | 35 |  | 64 | 28 | 2520 | 362.88 | 2016 | 56.448
CHS | 57 | 57 | 500 | 500 |  | Hallway | 2-F32T8 | 1x4 Wrap |  | 40 | 80 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 40 | (80)-F28T8 | (40)-2-F28T8 | Standard | Electronic IS | [7 empty] | 35 |  | 64 | 28 | 2520 | 3628.8 | 2520 | 0
CHS | 58 | 58 | 500 | 502 |  | Classroom | 2-F32T8 | 1x4 Wrap |  | 11 | 22 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 11 | (22)-F28T8 | (11)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 2160 | 855.36 | 1728 | 133.056
CHS | 59 | 59 | 500 | 500 |  | Offices | 2-F32T8 | 1x4 Wrap |  | 13 | 26 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 13 | (26)-F28T8 | (13)-2-F28T8 | Standard | Electronic IS | [7 empty] | 35 |  | 64 | 28 | 2400 | 1123.2 | 2400 | 0
CHS | 60 | 60 | 500 | 501 |  | Classroom | 2-F32T8 | 1x4 Wrap |  | 12 | 24 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 12 | (24)-F28T8 | (12)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 2160 | 933.12 | 1728 | 145.152
CHS | 61 | 61 | 500 | 504 |  | Classroom | 2-F32T8 | 1x4 Wrap |  | 12 | 24 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 12 | (24)-F28T8 | (12)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 2160 | 933.12 | 1728 | 145.152
CHS | 62 | 62 | 500 | 503 |  | Classroom | 2-F32T8 | 1x4 Wrap |  | 12 | 24 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 12 | (24)-F28T8 | (12)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 2160 | 933.12 | 1728 | 145.152
CHS | 63 | 63 | 500 | 506 |  | Classroom | 2-F32T8 | 1x4 Wrap |  | 12 | 24 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 12 | (24)-F28T8 | (12)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 2160 | 933.12 | 1728 | 145.152
CHS | 64 | 64 | 500 | 505 |  | Classroom | 2-F32T8 | 1x4 Wrap |  | 12 | 24 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 12 | (24)-F28T8 | (12)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 2160 | 933.12 | 1728 | 145.152
CHS | 65 | 65 | 500 | 508 |  | Classroom | 2-F32T8 | 1x4 Wrap |  | 12 | 24 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 12 | (24)-F28T8 | (12)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 2160 | 933.12 | 1728 | 145.152
CHS | 66 | 66 | 500 | 507 |  | Classroom | 2-F32T8 | 1x4 Wrap |  | 12 | 24 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 12 | (24)-F28T8 | (12)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 2160 | 933.12 | 1728 | 145.152
CHS | 72 | 72 | 400 | 400 |  | Classroom | 2-F32T8 | 1x4 Wrap |  | 2 | 4 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 2 | (4)-F28T8 | (2)-2-F28T8 | Standard | Electronic IS | [7 empty] | 20 |  | 64 | 28 | 2160 | 155.52 | 2160 | 0
CHS | 75 | 75 | 400 | 402 |  | Classroom | 2-F32T8 | 1x4 Wrap |  | 7 | 14 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 7 | (14)-F28T8 | (7)-2-F28T8 | Standard | Electronic IS | [7 empty] | 30 |  | 64 | 28 | 2160 | 544.32 | 2160 | 0
CHS | 76 | 76 | 400 | 403 |  | Classroom | 2-F32T8 | 8' Pendant Wrap |  | 12 | 24 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 12 | (24)-F28T8 | (12)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 25 |  | 64 | 28 | 2160 | 933.12 | 1728 | 145.152
CHS | 84 | 84 | Portables - 600 | 601 |  | Storage | 2-F32T8 | 2x4 Troffer |  | 12 | 24 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 12 | (24)-F28T8 | (12)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 20 |  | 64 | 28 | 360 | 155.52 | 288 | 24.192
CHS | 86 | 86 | Portables - 600 | 602 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 9 | 18 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 9 | (18)-F28T8 | (9)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 30 |  | 64 | 28 | 2160 | 699.84 | 1728 | 108.864
CHS | 88 | 88 | Portables - 600 | 604 |  | Offices | 2-F32T8 | 2x4 Troffer |  | 15 | 30 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 15 | (30)-F28T8 | (15)-2-F28T8 | Standard | Electronic IS | [7 empty] | 30 |  | 64 | 28 | 2400 | 1296 | 2400 | 0
CHS | 89 | 89 | 700 | 702 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 12 | 24 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 12 | (24)-F28T8 | (12)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 2160 | 933.12 | 1728 | 145.152
CHS | 90 | 90 | 700 | 701 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 12 | 24 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 12 | (24)-F28T8 | (12)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 2160 | 933.12 | 1728 | 145.152
CHS | 91 | 91 | 700 | 700 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 8 | 16 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 8 | (16)-F28T8 | (8)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 35 |  | 64 | 28 | 2160 | 622.08 | 1728 | 96.768
CHS | 92 | 92 | 800 | 801 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 12 | 24 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 12 | (24)-F28T8 | (12)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 30 |  | 64 | 28 | 2160 | 933.12 | 1728 | 145.152
CHS | 93 | 93 | 800 | 802 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 12 | 24 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 12 | (24)-F28T8 | (12)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 30 |  | 64 | 28 | 2160 | 933.12 | 1728 | 145.152
CHS | 94 | 94 | 800 | 800 |  | Restrooms | 2-F32T8 | 2x4 Troffer |  | 6 | 12 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 6 | (12)-F28T8 | (6)-2-F28T8 | Standard | Electronic IS | OS-1 | 1 | 2 |  |  |  |  | 30 |  | 64 | 28 | 2520 | 544.32 | 2016 | 84.672
CHS | 95 | 95 | 800 | 803 |  | Classroom | 2-F32T8 | 2x4 Troffer |  | 10 | 20 |  |  | Standard | Electronic IS | LED 14W Tubes |  | 10 | (20)-F28T8 | (10)-2-F28T8 | Standard | Electronic IS | OS-3 | 1 | 1 |  |  |  |  | 30 |  | 64 | 28 | 2160 | 777.6 | 1728 | 120.96
[11 empty] | 1340 | [22 empty] | 111820 | 51818.4

## ECM-4a V7a Calcs
Entire V7a Calculator for each site have been submitted as stand-alone documents

## ECM-4c Calcs
Site | ID | Source ID | Building | Room # | Plan ID | Room Type | Existing Fixture Type | Fixture Style | Fixture Height (ft.) | Existing Fixture Count (Single) | Existing Fixture Count (Tandem) | Old Fixture Burn Out Qty | Existing Lamp Type | Existing Ballast Type | Proposed Retrofit Type | Make and Model | Total Retrofit Qty | New Lamps Required | New Ballasts Required | New Lamp Type | New Ballast Type | Proposed Control Type | Control Qty | Relay Qty | Retrofit Complexity | Control Complexity | Ceiling Type | Notes | Foot Candles Before | Foot Candles After | Existing Watts Per Fixture | Proposed Watts Per Fixture | Hours of Operation Now | Retrofit Savings (kWh) | Hours of Operation After | Control Savings (kWh)
Egling | 15 | 15 | 100 | 102 |  | Classroom | 1-F32T8-U | 2x2 Troffer |  | 2 |  |  | Standard | Electronic IS | 1-F25T8-U |  | 2 | (2)-FB25T8 | (2)-1-F32T8-U | Energy Saving | Electronic IS | OS-3 | [6 empty] | 35 |  | 33 | 25 | 3650 | 58.4 | 2920 | 36.5
Egling | 17 | 17 | 100 | 101 |  | Classroom | 1-F32T8-U | 2x2 Troffer |  | 2 |  |  | Standard | Electronic IS | 1-F25T8-U |  | 2 | (2)-FB25T8 | (2)-1-F32T8-U | Energy Saving | Electronic IS | OS-3 | [6 empty] | 35 |  | 33 | 25 | 3650 | 58.4 | 2920 | 36.5
Egling | 30 | 30 | 100 | 119 |  | Classroom | 1-F32T8-U | 2x2 Troffer |  | 2 |  |  | Standard | Electronic IS | 1-F25T8-U |  | 2 | (2)-FB25T8 | (2)-1-F32T8-U | Energy Saving | Electronic IS | OS-3 | [6 empty] | 50 |  | 33 | 25 | 3650 | 58.4 | 2920 | 36.5
Egling | 32 | 32 | 100 | 120 |  | Classroom | 1-F32T8-U | 2x2 Troffer |  | 2 |  |  | Standard | Electronic IS | 1-F25T8-U |  | 2 | (2)-FB25T8 | (2)-1-F32T8-U | Energy Saving | Electronic IS | OS-3 | [6 empty] | 50 |  | 33 | 25 | 3650 | 58.4 | 2920 | 36.5
Egling | 36 | 36 | 100 | 129 |  | Classroom | 1-F32T8-U | 2x2 Troffer |  | 2 |  |  | Standard | Electronic IS | 1-F25T8-U |  | 2 | (2)-FB25T8 | (2)-1-F32T8-U | Energy Saving | Electronic IS | OS-3 | [6 empty] | 50 |  | 33 | 25 | 3650 | 58.4 | 2920 | 36.5
Egling | 40 | 40 | 100 | 100 |  | Classroom | 1-F32T8-U | 2x2 Troffer |  | 2 |  |  | Standard | Electronic IS | 1-F25T8-U |  | 2 | (2)-FB25T8 | (2)-1-F32T8-U | Energy Saving | Electronic IS | OS-3 | [6 empty] | 50 |  | 33 | 25 | 3650 | 58.4 | 2920 | 36.5
Egling | 67 | 67 | 200 | 214 |  | Classroom | 1-F32T8-U | 2x2 Troffer |  | 2 |  |  | Standard | Electronic IS | 1-F25T8-U |  | 2 | (2)-FB25T8 | (2)-1-F32T8-U | Energy Saving | Electronic IS | OS-3 | [6 empty] | 35 |  | 33 | 25 | 3650 | 58.4 | 2920 | 36.5
Egling | 70 | 70 | 200 | 210 |  | Classroom | 1-F32T8-U | 2x2 Troffer |  | 2 |  |  | Standard | Electronic IS | 1-F25T8-U |  | 2 | (2)-FB25T8 | (2)-1-F32T8-U | Energy Saving | Electronic IS | OS-3 | [6 empty] | 35 |  | 33 | 25 | 3650 | 58.4 | 2920 | 36.5
Egling | 75 | 75 | 200 | 203 |  | Classroom | 1-F32T8-U | 2x2 Troffer |  | 2 |  |  | Standard | Electronic IS | 1-F25T8-U |  | 2 | (2)-FB25T8 | (2)-1-F32T8-U | Energy Saving | Electronic IS | OS-3 | [6 empty] | 35 |  | 33 | 25 | 3650 | 58.4 | 2920 | 36.5
Egling | 77 | 77 | 200 | 204 |  | Classroom | 1-F32T8-U | 2x2 Troffer |  | 2 |  |  | Standard | Electronic IS | 1-F25T8-U |  | 2 | (2)-FB25T8 | (2)-1-F32T8-U | Energy Saving | Electronic IS | OS-3 | [6 empty] | 35 |  | 33 | 25 | 3650 | 58.4 | 2920 | 36.5
20
[33 empty] | TOTAL kWh Savings: | 584 |  | 365

## ECM-4d Calcs
Site | ID | Source ID | Building | Room # | Plan ID | Room Type | Existing Fixture Type | Fixture Style | Fixture Height (ft.) | Existing Fixture Count (Single) | Existing Fixture Count (Tandem) | Old Fixture Burn Out Qty | Existing Lamp Type | Existing Ballast Type | Proposed Retrofit Type | Make and Model | Total Retrofit Qty | New Lamps Required | New Ballasts Configuration | New Lamp Type | New Ballast Type | Proposed Control Type | Control Qty | Relay Qty | Retrofit Complexity | Control Complexity | Ceiling Type | Notes | Foot Candles Before | Foot Candles After | Existing Watts Per Fixture | Proposed Watts Per Fixture | Hours of Operation Now | Retrofit Savings (kWh) | Hours of Operation After | Control Savings (kWh)
CHS | 36 | 36 | 200 | Men's Locker Room |  | Locker Room | 2-F32T8 | 1x4 Wrap |  | 16 |  |  | Standard | Electronic IS | Sedona 43W LED |  | 8 | (8) 43W LED |  | LED | [10 empty] | 65 | 43 | 3500 | 616 | 2100 | 963.2
CHS | 43 | 43 | 200 | Women's Locker Room |  | Locker Room | 2-F32T8 | 1x4 Wrap |  | 22 |  |  | Standard | Electronic IS | Sedona 43W LED |  | 12 | (12) 43W LED |  | LED | [10 empty] | 65 | 43 | 3500 | 924 | 2100 | 1324.4
[10 empty] | 38 | [6 empty] | 20
[33 empty] | TOTAL kWh Savings: | 1540 |  | 2287.6

## ECM-5 Proj M1a
Colusa USD P39
ECM-5: Replace Wall Mount Heat Pumps
5a - Wall Mount AC w/ Electric Heat
List of Units
|  |  |  | Existing |  |  |  | Proposed
Site | Space Served | Unit Tag | Quantity | Capacity (tons) | Make | Model | EER | Capacity (tons) | Make | Model | EER
Colusa HS | 700 Wing (Portables) | #33-35 | 3 | 4 | Bard | n/a | 9 | 4 | Bard | T48HA | 11
Colusa HS | MPR | #3 a& 4 | 2 | 4 | Bard | n/a | 9 | 4 | Bard | T48HA | 11
Egling MS | P-1 (Portables) | #01 | 1 | 4 | Bard | n/a | 9 | 4 | Bard | T48HA | 11
Egling MS | P-2 to P-3 (Portables) | #02-03 | 2 | 3.5 | Bard | n/a | 9 | 3.5 | Bard | T42HA | 11
Egling MS | P-8 to P-9 (Portables) | #09-10 | 2 | 3.8 | Bard | n/a | 9 | 4 | Bard | T48HA | 11
Egling MS | P-4 (Portables) | n/a | 1 | 3.8 | Bard | n/a | 9 | 4 | Bard | T48HA | 11
Burchfield ES | Rm 19-23 (Portables) | #27-31 | 5 | 4 | Bard | n/a | 9 | 4 | Bard | T48HA | 11
|  | TOTAL | 16 | 27.1
Energy Savings per Unit
Capacity (tons) | (E) Unit Electricity Use | (N) Unit Electricity Use | Electricity Savings
| kWh | kWh | kWh
3.5 | 13092 | 9002 | 4090
4 | 13273 | 9010 | 4263
Savings and Cost per Site
Location | Nominal Tons | (E) EER | (N) EER | Qty | Annual Electric Savings | Annual Natural Gas Savings | Cost per Unit | Labor Cost per Unit | Annual Electic Savings
[5 empty] | kWh | therm |  |  | $$$
Colusa HS
700 Wing (portables) & MPR | 4 | 9 | 11 | 5 | 21315 |  | 5992 | 3500 | 3367.77 | Using $3,500 per District Direction
|  |  |  | 5 | 21315 | 0 | 29960 | 17500 | 3367.77
Egling MS
P-2, P-3 (portables) | 3.5 | 9 | 11 | 2 | 8180 |  | 5591 | 3500 | 1251.54
P-1, P-4, P-8, P-9 (portables) | 3.8 & 4 | 9 | 11 | 4 | 17052 |  | 5992 | 3500 | 2608.956
|  |  |  | 6 | 25232 | 0 | 35150 | 21000 | 3860.496
Burchfield ES
Rm 19-23 (portables) | 4 | 9 | 11 | 5 | 21315 |  | 5992 | 3500 | 4902.45
|  |  |  | 5 | 21315 | 0 | 29960 | 17500 | 4902.45
5b - Wall Mount AC w/ Gas Heat
List of Units
|  |  |  | Existing |  |  |  | Proposed
Site | Space Served | Unit Tag | Quantity | Capacity (tons) | Make | Model | SEER (EER) | Capacity (tons) | Make | Model | SEER (EER)
Colusa HS | 800 Wing (Portables) | #31-32 | 2 | 3.5 | Bard | n/a | (9) | 4 | Bard | WG4S | (11) | Note: Bard WG series sizes only come in whole ton increments (i.e. 3 or 4 ton)
Egling MS | P-5 to P-7 (Portables) | #06-08 | 3 | 3.2 | Bard | n/a | (9) | 3 | Bard | WG3S | (11)
Burchfield ES | Rm 3-7 (Portables) | #01-04 | 5 | 3.5 | Bard | n/a | (9) | 4 | Bard | WG4S | (11)
Burchfield ES | Rm 24-25 (Portables) | #25-26 | 2 | 3.5 | Bard | n/a | (9) | 4 | Bard | WG4S | (11)
|  | TOTAL | 12 | 13.7
Energy Savings per Unit
Capacity (tons) | (E) Unit Electricity Use | (E) Unit Natural Gas Use | (N) Unit Electricity Use | (N) Unit Natural Gas Use | Electricity Savings | Natural Gas Savings
| kWh | therm | kWh | therm | kWh | therm
3 | 9625 | 223 | 6834 | 222 | 2791 | 1
4 | 9709 | 245 | 6886 | 240 | 2823 | 5
Savings and Cost per Site
Location | (N) Nominal Tons | (E) EER | (N) EER | Qty | Annual Electric Savings | Annual Natural Gas Savings | Cost per Unit | Labor Cost per Unit | Annual Electic Savings
[5 empty] | kWh | therm |  |  | $$$
Colusa HS
800 Wing (Portables) | 4 | 9 | 11 | 2 | 5646 | 10 | 8391.04 | 3500 | 896.498 | Using $3,500 per District Direction
|  |  |  | 2 | 5646 | 10 | 16782.08 | 7000 | 896.498
Egling MS
P-5 to P-7 (portables) | 3 | 9 | 11 | 3 | 8373 | 3 | 7553 | 3500 | 1282.644
|  |  |  | 3 | 8373 | 3 | 22659 | 10500 | 1282.644
Burchfield ES
Rm 3-7, 24-25 (portables) | 4 | 9 | 11 | 7 | 19761 | 35 | 8391.04 | 3500 | 4573.73
|  |  |  | 7 | 19761 | 35 | 58737.28 | 24500 | 4573.73
28

## ECM 6
ECM 6 Skylights in CHS Gymnasium
Site | Location | Qty | Size | Materials (Skylight + Security Grill) | Labor | Tax/ Contingency | Annual Electrical Savings (kWh) | Energy Savings
CHS | Gymnasium | 19 | 4x4 | 350 | 100 | 100 | 0 | 0

## Uti Rates & Lighting Caps
Lookup Rate Sheet |  |  | Lighting Cap Calculations
School | Elec Rate | Gas Rate | Annual kWh | 15% Lighting Cap | T828W Retro | LED 14W Retro | LED Delta
Burchfield Primary | 0.23 | 0.82 | 238271 | 35740.65 | 14867 | 66829 | -31088.35
Egling MS | 0.153 | 0.525 | 440390 | 66058.5 | 23227 | 104320 | -38261.5
Colusa HS | 0.158 | 0.443 | 533847 | 80077.05 | 25273 | 70536 | 9541.05

## CPM ECM to DE Proj#
CPM ECM | ECM Description | Scope | Digital Energy Proj#
1a | Implement "automatic shutdown software on all computers. | Software and Programming | E-3
1b | PVC Strips added to Walk-ins |  | E-2
1c | VendingMisers |  | E-1
2 | Pelican Wireless Thermostats/Door Sensors | Replacement of all programmable thermostats with Pelican wireless thermostats including door sensors to cycle off HVAC equipment when door is left open. | M-5
3a | Lighting Exterior -Replacement of exterior Metal Halide (MH) fixtures with LED | MH 400W to LED 130W | L-6A
3b | Exterior Lighting Controls | Exterior Smart Controls | L-6B
4a | Interior Lighting Lamp Replacement | Replace T8 32W lamps with T8 28W lamps. Some U-type 32W to be replaced with 25W. | L-1
4b | Interior Lighting Lamp Replacement | Replace screw - in incandescent and compact fluroescent lamps with LED based screw in lamps. | L-2
5a | HVAC Pkg Gas/Elec Replacements | Replace all-electric wall-mount heat pumps with high efficiency units with economizers | M-1a
5b | HVAC Pkg Gas/Elec Replacements | Replace gas-heating wall-mount heat pumps with high efficiency units with economizers | M-1a